VOLUME 4

TECHNICAL SPECIFICATIONS

Table of Contest

0. GENERAL CONDITIONS	5

0.1 Location of the Sites	5

0.2 Scope of the work	5

0.3 Contractor’s responsibility	5

0.4 Temporary works and Reinstatement	5

0.5. Subsurface utilities	5

0.6. Watching	5

0.7 Water and electric power for the works	5

0.8. Medical facilities	5

0.9. Specified manufacturer products	6

0.10. Alternative material	6

0.11. Imported material	6

0.12. Periodic reports	6

0.13. Site progress meeting	6

0.14. Care of the works	6

0.15. Clearing away	6

0.16. Construction Generally	7

0.17. Removal works	7

0.18. Disposal of Materials	7

0.19. Testing by the Contractor	7

0.20. Quality Assurance	7

0.21. Inspection	7

0.22. Suppression of noise and pollution	8

0.23. Protective equipment and clothing	8

0.24. Safety on Site	8

0.25. Project planning and scheduling	8

0.26. Submissions to the Supervisor	8

0.27. Offices for the Supervisor and Contractor’s staff	8

0.28. Applicable standards	9

0.29. Communication and visibility in EU – financed external actions	9

1. CIVIL WORKS	10

1.1. DEMOLITION/REMOVAL WORKS	10

1.2. EARTHWORKS	10

1.2.1. Excavation and filling (backfilling)	10

1.3 CONCRETE WORKS	11

1.3.1 Formwork for concrete	12

1.3.2 Design of concrete mixes	13

1.3.3 Mixing concrete	14

1.3.4 Admixtures	15

1.3.5 Transport of concrete	15

1.3.6 Placing of concrete	15

1.3.7 Compaction of concrete	16

1.3.8 Curing of concrete	16

1.3.9 Cement Screeds	17

1.4. REINFORCEMENT	17

1.5. METAL WORKS	17

S235	18

S275	18

1.6. MASONRY	18

1.6.1 Mortar	18

1.6.2. Walls of bricks and ceramic blocks (hollow)	18

1.7. SANDWICH PANNELS AND TINSMITH WORKS	18

1.7.2. Steel sheet gutters	19

1.7.3 Rainwater outlets	19

1.7.4 Rainwater down pipes:	19

1.8. INSULATION WORKS	20

2. CRAFTSMEN WORKS	23

2.1. FINISHING WORKS	23

2.1.1	FLOOR FINISHING WORKS	23

Site Preparation & Placement Environment	23

2.1.2 WALL FINISHING WORKS	24

2.5. FAÇADE WORKS	28

2.5.1 Stone wall	28

4. INSTALLATIONS WORKS	29

4.1. WATER SUPPLY, FIRE PROTECTION and WASTE WATER	29

General	29

Water Supply	29

4.1.1-1. Polypropylene PPR pipes	30

4.1.2. Galvanized tubes	31

4.1.3. Ductile pipes with standard joints certified for potable water	31

4.1.4. Testing the pipeline	31

4.1.5. Hydromechanical equipment	31

4.1.5.8. Protection of water lines	33

4.1.5.9. Electric water heaters for hot sanitary water	34

4.1.5.10. Water flow meter	34

4.1.5.11. Fire cabinets	34

4.1.5.12. Testing and commissioning	34

4.1.5.13. Sanitary Fixtures	34

4.1.5.15. Testing of sanitary fixtures	35

4.2. Waste Drainage Installation	35

4.2.1 Piping	35

4.2.2 Piping and Fittings Materials	36

4.2.3. Ventilating	36

4.2.4 Flashings	36

4.2.5 Manhole cover with a circular shape	36

4.2.6 Testing and commissioning	36

4.2 ELECTRICAL INSTALATIONS WORKS	36

Е.1 EXTERNAL ELECRTICAL INSTALLATION	40

E 1.1 SITE PREPARATORY WORKS	40

E 1.2 ALIGNMENT WORKS	40

E.1.6 EARTHING INSTALLATION	42

E 1.10 FINAL PHASE -BUILT STAGE	44

As buit drawings	44

E 2.1 SITE PREPARATORY WORKS	48

E 2.2 SUPPLY SYSTEM- DISTRIBUTION BOARD	48

E 2.7.1 SOCKET	54

E 2.7.4  JUNCTION BOXES	56

- Junction boxes for wall mounting - F78, 100x100, 100x150 with technical characteristics	56

• Insulation class according to IEC 61140	56

• Mechanical resistance IK 08	56

• Type of material – halogen-free, in accordance with EN 60754-2	56

• Thermal pressure with ball 850 C	56

• 6500C heated wire test	56

• Operating temperature -25 to +600 C	56

- Junction boxes for wall mounting: 100x100, 100x150 with technical characteristics	56

E 2.8 ELECTRIC LIGHTING	56

ANTI-PANIC LED LAMP TYPE1	57

ANTI-PANIC LED LAMP TYPE2	57

MOTION SENSOR	57

E 3. LOW CURRENT SIGNAL ELECTRICAL INSTALLATION AND EQUIPMENT	58

E.3.1 FIRE ALARM SYSTEM AND ACCESSORIES SYSTEM	58

E.5. DIESEL GENERATOR	66

Composition	66

System Conditions	67

Standards	67

Ratings:	67

Performance	68

Diesel Engine	68

Speed Governor:	68

Shutdown System:	68

Cooling System:	68

Pumps:	68

Lubrication:	68

Safety Guards:	68

Fuel:	68

Lubricating and Fuel Oil Filters:	68

Air Filters:	68

Starting System:	68

Exhaust System:	68

Alternator	69

Automatic Transfer Switch (ATS)	69

Mounting	69

Fuel Tanks	69

Concrete foundation /pad drawings	69

4.4. FIRE FIGHTING	73

# 0. GENERAL CONDITIONS

Read these Specifications in conjunction with the Drawings, the Bill of Quantities and other Contract Documents.

The Contractor must, in due time, before the start of the works, inform the Supervisor about the preparatory works of the Contractor itself and other Sub - Contractors, and must devise a time deadlines for the completion of the works.

## 0.1 Location of the Site

The site of the Works is located in Markova Noga in the Republic of North Macedonia (Border crossing point Markova Noga-Lemos, CM Dolno Dupeni, Municipality of Resen).

## 0.2 Scope of the work

The works to be carried out under this Contract shall include but not be limited to the complete Reconstruction with upgrade and extention of the State Border Police Station at Markova Noga, as shown on the Drawings and as described in these Specifications.

## 0.3 Contractor’s responsibility

The Contractor shall bear, at his own cost the entire responsibility for the sufficiency of plant, scaffolding, machinery, tools labour, etc and for all means used for the execution of the fulfilment of the Contract which may be or may not be approved by the Supervisor.

Notwithstanding any minimum requirements included in this specification regarding the quantity, output and adequacy of plant and outline of methods, the attaining of the specified standards of quality of work shall be the sole responsibility of the Contractor.

## 0.4 Temporary works and Reinstatement

The Contractor shall submit full particulars of all Temporary works to the Supervisor before commencing same. The Supervisor may require modifications and the Contractor shall give effect but shall not be relieved of his responsibilities for the sufficiency thereof.

The Contractor shall provide and maintain weatherproof storage of materials pertinent to the works and clear same away at the completion of the Works.

The Contractor shall make good, at his own expense, all damage to utilities. The cost incurred shall be paid by the Contractor.

All injury to the surface of the land, where disturbed by the works, shall be repaired by the Contractor at his expense.

The requirements above shall be provided and maintained at the expense of the Contractor.

## 0.5. Subsurface utilities

It shall be the responsibility of the Contractor to determine the exact location of pipelines, subsurface structures and utilities ahead of his work and to take suitable precautions to prevent damage and interruption of services which such facilities provide.

## 0.6. Watching

The Contractor shall allow for all necessary watching for the security of the works and the protection of the public.

## 0.7 Water and electric power for the works

The Contractor shall provide all necessary water and electrical power for the works and pay for their use and remove and make good at completion if necessary.

## 0.8. Medical facilities

The Contractor shall arrange for medical attention to be available and shall provide adequate FIRST Aid equipment within easy access of each work area.

## 0.9. Specified manufacturer products

It shall be understood that actual material supplied shall meet the requirements of the specifications and if necessary, the material specified shall be modified under the direction of the Supervisor.

## 0.10. Alternative material

Should the Contractor wish to offer alternative items to those specified he shall submit details of such alternative with details of any impact on the contract price if the alternative is allowed to be substitute for the specified items or materials and shall comply fully in all respects with the specifications of the particular items or materials.

The acceptance or refusal of such alternative shall be entirely at the discretion of the Supervisor.

If during the course of the Contract certain materials or items required for use in the works should be unobtainable the Contractor may offer for the approval of the Supervisor  alternative item or material provided they possess the minimum requirements of the finally specified material. If the alternative material is accepted no price addition shall be approved in respect of the increase in the value.

In case of refusal of any material or item the Contractor shall not be relieved of any of his obligations under the Contract and shall be solely fiable for any delay or loss occasioned by his failure to provide the material or item as specified.

## 0.11. Imported material

The Contractor is required to submit documentary evidence that all imported material or item is ordered shortly after the Site is handled over for the commencement of the work. Copies of such orders shall be submitted to the Supervisor.

## 0.12. Periodic reports

The Contractor must present to Supervisor detailed reports and schedules on a monthly basis or as stipulated in the Conditions of Contract without having the right to use such report document to support a claim for any extra payment or compensation whatsoever in regard or in relation to such reports.

## 0.13. Site progress meeting

The Site progress meeting shall be held at regular intervals at least once every two weeks in the presence of the Supervisor to coordinate the Contractor works insuring the full compliance with the various sequences are maintained. Minutes of such Site meetings will be recorded and copies will be distributed to all concerned and full effect shall be given to all instructions contained herein.

Prior to such meeting the Contractor shall give to the Supervisor in writing the portion of the works he proposes to realize during the coming two weeks with details of methods to employ. The proposals shall be discussed at the meeting and no work based on such proposal shall proceed without the approval of the Supervisor.

## 0.14. Care of the works

The Contractor shall keep all persons under control and shall be responsible for the care of existing premises and of the works until their completion, including all work and materials, goods and plant on the Site including all risks arising from the weather, carelessness of work people, damage or loss by theft or any other cause and he shall make good at his own expense all such damage or loss.

## 0.15. Clearing away

The Contractor shall take down and clear away all temporary works, debris and surplus materials from the Site as they accumulate and at completion and clean surfaces internally and externally, remove stains and touch up paint work and leave the works clean and to satisfaction of the Supervisor at completion.

## 0.16. Construction Generally

- The Contractor shall be responsible for the location of suitable sources of materials for the execution of the works, except where otherwise specified, whether such sources are on the site or not and for obtaining all necessary permissions.

- Materials available on the site shall be used for the execution of the works.

- Structures, which are to remain intact, shall be properly located, adequately supported, protected and maintained. Services shall be similarly treated, unless a diversion is deemed necessary, in which case it shall be carried out in a manner that prevents inconvenience to the owner and ensures the continuity and safety of the services concerned.

- The Contractor shall not pollute roads, lands and other places on the site.

- The Contractor shall provide and maintain adequate communications around the site.

The Contractor must keep a Construction Diary at the construction site in accordance with the Beneficiary legislation. This log must contain all changes and deviations from the main design. The Construction Diary shall be signed and stamped by the Contractor and the Supervisor.

## 0.17. Removal works

The Contractor’s work plan shall set all of these demolition works in such a manner as to minimize the risk of rain ingress into the structure with the use of suitable temporary covering.

All external and internal walls, part of the floor slabs, floor finishes which are foreseen to be demolished shall be taken down carefully so as to minimize dust and disruption to other parts of the structure. The debris arising from demolition shall be disposed of to an approved dumping area.

Windows and internal doors marked on the drawings to be disassembled shall be removed carefully and stored in a safe manner.

Where plaster is damaged both in the existing condition and as a result of the demolition works it shall be repaired in proper way.

## 0.18. Disposal of Materials

The Contractor shall not dispose of materials of any kind obtained from the site without the permission of the Supervisor. Debris shall be removed only to dumping areas approved by local authorities. For dismantled items and materials which Contracting Authority/Supervisor will decide to keep and store them.

## 0.19. Testing by the Contractor

The Contractor shall provide throughout the whole period of execution of the works, as requested by the Supervisor, all necessary tests for the control of the materials and workmanship, in accordance with this Specification. If necessary, the Contractor shall have such tests carried out by an independent organization, acceptable to the Supervisor.

## 0.20. Quality Assurance

The Contractor, his suppliers and other sub-contractors shall comply with the Quality Standards set out in the Conditions of Contract in all respects. Copies of the quality plan, records and other documentation, shall be submitted to the Supervisor, in regard to imported materials and before such materials arrive on the site.

## 0.21. Inspection

In respect to all items of equipment and materials to be imported for incorporation in the permanent works the Contractor shall submit to the Supervisor, in English language, inspection and test reports certified by an independent organization of international repute. The reports shall certify that all such items are in full compliance with the Contract requirements and specifications.

The Supervisor shall be entitled to apply the Conditions of Contract in respect of items not so certified. The certification shall be furnished at the Contractor expense. It shall not relieve the Contractor of the obligation to ensure that all materials and workmanship incorporated in the works shall be in full compliance with the Contract requirements and specification at the time of final handling over of the completed works.

## 0.22. Suppression of noise and pollution

The Contractor shall make every reasonable endeavor to ensure that the level of noise or pollution resulting from the execution of the works does not constitute a nuisance. The Contractor shall undertake all such precautions as may be necessary in the conduct of the work to avoid water pollution, air pollution, noise pollution harmful to health, spreading of diseases or damage to natural resources or the environment, all as is consistent with good practice and as required by applicable laws, ordinances, regulations or lawful order of authorities having jurisdiction.

## 0.23. Protective equipment and clothing

The Contractor shall provide and maintain all necessary protective and safety equipment and clothing for the operative and Site staff.

## 0.24. Safety on Site

Safety on site shall be a prime consideration of the Contractor who is to appoint a Safety Supervisor throughout the contract. This person is to provide the Supervisor with weekly reports on safety of all operations including regular inspection reports on all site equipment and scaffolding and the storage of hazardous materials.

The Contractor is to ensure that all persons working on the site are to have adequate personal protective clothing. He has also to provide with helmets Supervisor’s staff when visiting the site.

## 0.25. Project planning and scheduling

In accordance with the Conditions of Contract, the Contractor shall submit to the Supervisor detailed programmes for the execution of the works, showing the order in which the various sections of the work are to be constructed, and in so shall take account of the restrictions and limitations described in this Specification. Once accepted by the Supervisor, the programmes shall be strictly followed, unless any alterations are found necessary during the construction and confirmed by the Supervisor.

The Contractor shall state and allow a reasonable margin of time for the contingencies Works.

## 0.26. Submissions to the Supervisor

Wherever these Specifications require, the Contractor shall submit to the Supervisor proposals, details, calculations, information, materials, test reports, certificates, etc. The Supervisor will consider each submission and shall reply to the Contractor in accordance with the relevant provision of the Contract Conditions.

No operation shall be carried out without complete notice having been given to the Supervisor by the Contractor, sufficiently in advance of the time of the operation to enable the Supervisor to make such arrangements as he may deem necessary for its inspection and checking.

The approval of the Supervisor of any submission shall not relieve the Contractor from his responsibilities under the Contract.

## 0.27. Offices for the Supervisor and Contractor’s staff

The Contractor shall provide offices at site for his own staff and for Supervisor’s team.

The office for Supervisor will be equipped with furniture as follows:

- 1 cabine as office

- 1 computer:
CPU: Intel Core i7-1165G7 (4C / 8T, 2.8 / 4.7GHz, 12MB)

RAM: 8GB SO-DIMM DDR4-3200 + 4GB Soldered DDR4-3200

One memory soldered to systemboard, one DDR4 SO-DIMM slot, dual-channel capable

Max Memory: Up to 16GB (8GB soldered + 8GB SO-DIMM) DDR4-3200

SSD: 512GB SSD M.2 2242 PCIe 3.0x4 NVMe

GPU: Integrated Intel Iris Xe Graphics

Display: 17.3" FHD (1920x1080) IPS 300nits Anti-glare, 72% NTSC

Ports:

Standard Ports

1x Power connector

1x Card reader

1x USB 3.2 Gen 1

1x HDMI 1.4b

1x Headphone / microphone combo jack (3.5mm)

1x USB 2.0

- 1 A4 format printer

- 2 desks

- 4 stools

- Software: MS Office 2021, MS Project 2019, AutoCAD 2021

- Car - one 4-wheel-drive vehicle. The cost of the vehicle, fuel and maintenance of the vehicles shall be borne by the Contractor.

The exact location of the temporary site offices will be defined by the Supervisor after consultation and agreement with Beneficiary representative and Administration. The Contractor shall within 2 weeks of being ordered to do so hand over to the Supervisor office accommodation fully equipped as specified.

The cost of office running shall be borne by the Contractor and shall be included in the Bill of Quantities.

All the equipment, provided to the Supervision staff for his personal during the implementation of the works shall remain property of the Works Contractor. The assets will be returned back to the Contractor within one month after the date of the Provisional Acceptance for the Works.

## 0.28. Applicable standards

In this technical specification, relevant MKS standards are in use as well as related EN, ISO, DIN and BS.

## 0.29. Communication and visibility in EU – financed external actions

The Communication and Visibility Manual for European Union External Actions set out the compulsory requirements for all contractors and implementing partners.

Applicants must comply with the objectives and priorities and guarantee the visibility of the EU financing (see the Communication and Visibility Manual for EU external actions specified and published by the European Commission Annex 1 – Volume 4).

All visibility events as well as materials produced within the EU-funded project need to incorporate mandatory information that actions are wholly or partially funded by the European Union (EU), as follows: EU logo, the title of the project and the sentence: "This project is funded by the European Union".

Furthermore, EU-funded projects need to prepare a project summary, based on the guidelines provided in the attached template, at the beginning of project implementation. A revised version of the project summary should also be provided at the end of project's implementation, reflecting project's achievements, as well as statement by the beneficiary.

Before initiating any information, communication or visibility activity, contractors, implementing partners and international organisations should contact the EU Delegation, Press and Information Officer and Task Manager of the EU-funded project.

The EU Delegation should always be invited to participate in visibility and communication events.

The relevant Contracting Authority is in any event responsible for monitoring the successful implementation of all visibility provisions

The Contractor shall install signboards at construction site with minimum dimension of 1.5/1.7 m. The information boards shall be in compliance with the Communication and Visibility Manual for EU external actions (Annex to item G.1.2 – Signboard – Template)) and complied with standards of the Beneficiary Country. Design of signboards shall be agreed upon with the Employer and the Engineer prior to posting.

The Visibility requirements of CBC Programme should be respected as well.

# 1. CIVIL WORKS

## 1.1. DEMOLITION/REMOVAL WORKS

1. Requirements

- Dust control.	Take appropriate action to check the spread of dust and avoid the creation of a nuisance in the surrounding area. Comply with all dust regulations imposed by the local air pollution agencies.

- Protection of existing works.	The existing works which shall remain in place or be reused or remain the property of the Beneficiary shall be protected using temporary covers, bracing or supports. Items to be damaged during the performance of the work shall be repaired to their original condition.

- Safety.    Where a safety is endangered by the demolition work, use appropriate signs to redirect from the demolition area.

2. Execution

- Existing utilities and related equipment.	  Careful removal of existing utilities with termination in a manner conforming to local regulations covering the specific utility and as approved by the Supervisor.

3. Disposal and title of materials.

- The doors and windows to be removed for the implementation of the contract shall remain the property of the beneficiary and the Contractor shall be requested to provide proper disposal of the same.

- Material debris and equipment to be removed shall be property of the Beneficiary in its proper form.

## 1.2. EARTHWORKS

### 1.2.1. Excavation and filling (backfilling)

This section covers all excavation and filling operations forming part of the permanent Works.

Prior to the excavation, the Contractor must satisfy himself that there are no existing services in the area.

The Contractor is required to expose the base of the excavation for foundations and arrange for the Supervisor’s Representative to have it inspected prior to covering it with the first blinding layer of concrete. If the ground is not found to be satisfactory for the proper support of the foundation without unacceptable settlement then the Contractor is to excavate down to a firm stratum and backfill with mass concrete or take other measures as are necessary to ensure an adequate foundation for the structure.

Filling of the ground beneath the slabs and foundations shall be done by first well compaction the existing ground and placing layers, in thickness of 200 mm, of adequately graded well-compacted quarry aggregate filling material.

After concreting of foundations all excavated areas around foundations shall be backfilled with suitable stockpiled material, well compacted in layers of 200mm and the surfaces shall be reinstated as appropriate.

All service cables and pipes shall be surrounded with sand bed to prevent them from being damaged by sharp stones. There also shall be warnings strips and the trenches shell be refilled and compacted with suitable excavated material and the surfaces shall be reinstated as appropriate.

1. Trenches for Services

Trenches for pipework shall be so excavated as to allow the pipes to be properly laid to line and level, jointed, inspected and tested. The width of all trenches from the bottom of the trench to the crown of the pipe shall be no wider than is necessary to permit the correct jointing of the pipes laid in the trench, but in no case shall the clearance between the outside of the barrel of such pipes and the face of the excavation or trench supports be less than 150 mm.

Trenches for pipework shall be excavated below the invert level of the pipe to a depth that will allow the minimum thickness of bedding material or concrete as shown on the Drawings to be placed.

Sufficient bedding material (sand) shall be placed in the trench to permit the pipes, when adjusted to their correct line and level, to be supported along at least three-quarters of their length before the remainder of the granular bedding material is placed.

The layer of sand shall be with a grain size of 4 to 8mm in a layer of minimum 10 cm from and the   laying of the pipes should be even, so the surface of the substrate should be scaled with an accuracy of ± 1.0cm.

In the shafts (manholes), a layer of sand of a grain size of 4 to 8.0mm from a natural non separated material in a layer of up to 10 cm should be placed.

The material should be compacted with a vibration-free roller, up to 95% compactness, determined according to standard Proctor-experiments at optimum humidity.

Trenches for cables shall be the minimum width necessary for the correct installation of the cables.

2. Backfilling

The filling shall be carried out in accordance with the technical conditions for carrying out embankments of natural material, standardized in MKS (JUS) U.C5.020. Rough and fine planning will be done manually and mechanized.

The drainage of the trenches should also be with a material as cleaned stones or any sharp objects that can damage the pipe, especially this refers to the first 30 cm above the tube that is actually a protective layer. The deposition and compacting should be performed in layers of 30 cm in height min. 1 m above the upper edge of the pipe, and above this height of the remaining part of the embankment in the space in width and height it is allowed the use of compaction machines such as light compacting tools.

3. Compacting

After filling in layers, it is necessary to compress each layer separately. The compacting can be manually or mechanically, with crossings several times over the layer of embedded material until a satisfactory compactness must be obtained that must be controlled.

When compacting the materials, a permanent geomechanical control shall be performed by a field geomechanical laboratory. Geomechanical control will be performed according to a special program, which includes control of the thickness of the built-in layers, the quality of the material that is being built and the achieved values ​​of the installation.

The compacting is done until that moment, which is of 90% to 92% compressibility determined according to the standard Proctor- experiment at optimum humidity.

## 1.3 CONCRETE WORKS

Reference: UNI 6126-72; UNI 6127-80 ; UNI 6131-87 ; UNI 6132-72 ; UNI 7101-80 ; UNI 7103-72 ; UNI

7163-79 ; UNI 9418-89 ; UNI EN 206 UNI EN 1008, EUROCODE 2 - EC2

General

All concrete work shall be carried out fully in accordance with the Design, Static Analysis and applicable regulations and standards.

The concrete shall be mixed mechanically from aggregate, cement and water, subject to the Supervisor approval, following the authoritative regulations for reinforced concrete in R.Macedonia.

The aggregate has to be clean, without organic impurities, or earth (acceptable up to 2% by weigh), otherwise the aggregate has to be washed.

The Contractor shall be under obligation to present evidence on quality of material used for concrete manufacturing (cement, aggregate, water).

The concrete quality and executed works have to be in accordance with prevailing regulations.

The concrete works shall be executed by qualified work force only, respecting technical specifications and prevailing regulations, national and international standards for such type of works.

Prescribed number of samples shall be tested by an Institute for Construction Material Testing on the Contractors expense. The Supervisor shall be entitled to request additional sample testing, up to the maximal number of samples foreseen under the regulation, fee of any additional expense on his side, if the Supervisor should request additional sample testing, exceeding the maximal number of samples foreseen under the regulation, then in case of unsatisfactory test results expenses shall be on the Contractor, otherwise, in case of positive test results, the Contractor shall bear expenses of such additional testing.

Concreting shall not commence prior to the inspection and acceptance of the reinforcement by the Supervisor.

Only plain concrete casting shall be done manually in 5-15 cm layers, the reinforced concrete casting shall be done mechanically with vibration, provided that a vibration equipment shall be in accordance with the type of structure, subject to the Supervisor approval.

There are following the newly introduced standard that defines 28 days compressive strength [ N/mm² ] using, either a cylinder Ø 15 cm/30 cm test sample, or a 15 cm cube test sample, compared to the 20 cm cube test sample.

Blinding concrete, grade C15 (15 N/mm2 compressive strength at 28 days) shall be placed over all excavations, which shall receive reinforced concrete.

### 1.3.1 Formwork for concrete

Formwork shall be constructed so it will support the loads imposed on them by the fresh concrete together with additional stresses imposed by vibrating equipment and by construction traffic, so that after the concrete has hardened the formed faces shall be in the positions shown on the Drawings within the tolerances set out in Eurocode 2.

All joints in formwork shall be tight against the escape of cement and fines. Where reinforcement projects through formwork, the form shall fit closely round the bars.

Formwork shall not be re-used after it has suffered damage, which is sufficient to impair the finished surfaces of the concrete.

Formwork shall be designed that it may be easily removed from the work without damage to the faces of the concrete. It shall also incorporate provisions for making minor adjustments in position, if required, to ensure the correct location of concrete faces.

Before any reinforcement is placed into position within formwork, the latter shall be thoroughly cleaned and then dressed with a release agent. The agent shall be either suitable oil incorporating a wetting agent, an emulsion of water suspended in oil or low viscosity oil containing chemical agents. The Contractor shall not use an emulsion of oil suspended in water nor any release agent, which causes staining, or discolouration of the concrete, air holes on the concrete surface, or retards the set of the concrete.

Before concrete placing commences, all wedges and other adjusting devices shall be secured against movement during concrete placing and the Contractor shall maintain an observation on the formwork during placing to ensure that no movement occurs.

Formwork shall be carefully removed without shock or disturbance to the concrete. No formwork shall be removed until the concrete has gained sufficient strength to withstand safely any stresses to which it may thereby be subjected.

Defective surfaces shall not be made good by plastering

The minimum periods which shall elapse between completion of placing concrete and removal of forms are given in the Table below;

| Position of Formwork | Min period for temps. over 100 C | Strength to be attained |
| --- | --- | --- |
| Vertical or near vertical faces of mass concrete | 24 hours | 0.2 C |
| Vertical or near vertical faces of reinforced walls, beams and columns | 48 hours | 0.3 C |
| C is the nominal strength for the class of concrete used. |  |  |

Note: Compliance with these requirements shall not relieve the Contractor of his obligation to delay removal of formwork until the removal can be completed without damage to the concrete.

Slab foundation plane concrete bedding th=10 cm, C15

Procurement of material and casting of C15 plane concrete bedding d=10 cm for the Pool foundation slab and plane concrete d=5 cm as a protection of slab foundation’s waterproofing. The bedding shall be compacted with top surface fine levelled.

Wall & slab reinforced concrete foundation

Procurement of material and casting of a C25 reinforced concrete slab foundation walls th=30 cm. The Pool wall shall be made and reinforced according to the Design, following reinforcement details and the Static Analysis. Required shuttering shall be provided. The concrete shall be cast and cured as prescribed under the regulations and standards. Price of shuttering included.

Reinforced concrete walls C25, executed in flat formworks

Procurement of material and casting of the C25 reinforced concrete walls, d=20 cm. The walls shall be reinforced according to the Design, reinforcement details and the Static Analysis; the concrete shall be cast into double sided shuttering and cured as prescribed under the regulations and standards.

### 1.3.2 Design of concrete mixes

(a) Classes of concrete

| Grade of concrete | Min Cement Content kg/m3 | Max W/C ratios |  | 150 mm cubes required min average 28 day strength (MAS) N/mm2 |
| --- | --- | --- | --- | --- |
|  |  | A | B |  |
| C15 | 250 | 0.57 |  | 27 |
| C20 | 300 | 0.53 | 0.50 | 28.5 |
| C25 | 360 | 0.49 | 0.46 | 31.5 |

Note:	MAS = Required Minimum Average 28 day strength, MB = C Concrete grade symbol

(b) Design of proposed mixes

The Contractor shall design the mixes which he proposes to use in the Permanent Works to achieve acceptable workability and resistance to segregation during handling and placing. Mixes shall also comply with the following requirements:

- The aggregate portion shall be well graded from the nominal maximum size of stone down to the 150 micron size.

- The cement contents shall be as designated in Table above unless higher cement content is required to meet the strength requirement.

- The water/cement ratio shall be the minimum consistent with adequate workability but in any case not greater than that shown in Table above taking due account of any water contained in the aggregates.  The Contractor shall take into account that this requirement may need the inclusion of a workability agent in the mix.

- The workability shall be consistent with ease of placing and proper compaction having regard to the presence of reinforcement and embedded items.

- The crushing strength at 28 days as determined in accordance with Item “Design of concrete mixes for structural concrete” shall not be less than the minimum average strength given in Table above plus 2 N/mm2.

- The drying shrinkage determined in accordance with EN 1992-1-1:2004+AC2:2010 Section 3.1.4 & Annex B shall not be greater than 0.05 per cent.

The Contractor shall submit full details of all the mixes he proposes to use to the Supervisor.

(c) Trial Mixes with 150 mm test cubes

For each mix of concrete the Contractor shall in the presence of Supervisor prepare three separate batches of concrete using the materials which have been approved for use in the permanent Works and the mixing plant which he proposed to use for the permanent Works.

The marking, curing and testing of all test cubes shall comply with the requirements of EC2.  The slump of the concrete carried out in accordance with EN12350-2 shall be recorded.

Three cubes from each batch shall be tested for compressive strength at seven days and the remaining three at 28 days.

The density of all the cubes shall be determined before the cubes are crushed. The average value of the crushing strength of the nine cubes tested at 28 days less 2 N/mm2 shall be greater than the Minimum Average Strength given in Table above for the grade of concrete tested.

If the 28 day strength determined as above is less than the minimum average strength shown in Table 2 plus 2 N/mm2 the mix shall be adjusted in order to comply.

If the Supervisor does not agree to a proposed concrete mix for any reason, the Contractor shall amend his proposals and carry out further trial mixes. No mix shall be used in the permanent Works without the written consent of the Supervisor’s Representative.

Based on the results of the tests on the trial mixes, the Contractor shall submit full details of his proposals for mix design to the Supervisor, including the type and source of each ingredient, the proposed proportions of each mix and the results of the tests on the trial mixes.

(d) Quality control of concrete production

For each grade of concrete in production at each plant for use in the permanent Works, samples of concrete shall be taken at the point of mixing or of deposition as instructed by the Supervisor and in the presence of a representative of the Supervisor, all in accordance with the sampling procedures described in МКS EN206:2014+A1:2017.

The slump of each sample carried out in accordance with МКS EN206:2014+A1:2017 shall be determined at the time of sampling.

Samples shall be taken on the basis of not less   than one sample per day or one sample for each pour of concrete placed, whichever is the more frequent. Three 150 mm test cubes shall be cast from each sample, cured and tested as set out in МКS EN206:2014+A1:2017. One cube shall be tested at seven days and two at 28 days. The average strength of the two cubes crushed at 28 days shall be referred to as one test result.

(e) Failure to comply with requirements

The Contractor shall take any action instructed by the Supervisor to remedy concrete which fails to comply with the Specification. Such action may include but is not necessarily confined to the following:

- Carrying out additional works to overcome the effect of the failed concrete.

- Removing the failed concrete.

### 1.3.3 Mixing concrete

Before any plant for batching, mixing, transporting, placing, compacting and finishing concrete is ordered or delivered to Site, the Contractor shall submit to the Supervisor full details including drawings of all the plant which he proposes to use and the arrangements he proposes to make.

Concrete for the permanent Works shall be batched and mixed in one or more central plants unless the Supervisor agrees to some other arrangement.

Batching and mixing plants shall be modern efficient equipment complying with the requirements MKS EN-12620 and capable of producing a uniform distribution of the ingredients throughout the mass. Track mixers shall not be used unless the Supervisor agrees otherwise. If the plant proposed by the Contractor does not fall within the scope of MKS EN-12620, it shall have been tested and shall have a mixing performance within the limits of MKS EN-12620.

Cement and aggregates shall be batched by weight. Water may be measured by weight or volume.

The weights of cement and of each size of aggregate indicated by the equipment and shall be within a tolerance of plus or minus two per cent of the respective weights per batch agreed by the Supervisor.

The nominal drum capacity of the mixer shall not be exceeded. The turning speed and the mixing time shall be as recommended by the manufacturer, but in addition, when water is the last ingredient to be added, mixing shall continue for at least one minute after all the water has been added to the drum or pan.

The water to be added to the mix shall be reduced by the amount of free water contained in the coarse and fine aggregates. This amount shall be determined by the Contractor by a method agreed by the Supervisor immediately before mixing begins each day and thereafter as the Supervisor directs. When the correct quantity of water, determined as set out in the Specification, has been added to the mix, no further water shall be added, either during mixing or subsequently.

After mixing for the required time, each batch shall be discharged completely from the mixer before any materials for the succeeding batch are introduced.

### 1.3.4 Admixtures

General

The use of admixtures in concrete may be required under the Contract to promote special properties to the concrete or may be proposed by the Contractor to assist compliance with the Specification.

In all cases the Contractor shall submit to the Supervisor full details of the admixture he proposes to use and the manner in which he proposes to add it to the mix.

The chloride ion content of any admixture shall not exceed 2% by weight of the admixture nor 0.03% by weight of the cement in the mix.

Admixtures shall not be mixed together without the consent of the Supervisor.

Super plasticizing admixtures

Super plasticizing admixtures shall comply with MKS U.M1.035. If the super plasticizing additive is not specified but the Contractor requests permission to use it the Supervisor shall not approve its use unless full particulars including chemical constituents of the admixture are submitted and the additional trial mixes mentioned above have been carried out and all are considered satisfactory. The Supervisor reserves the right to refuse the use of super plasticizing admixture for concrete required for particular structures.

Workability agents

Subject to the agreement of the Supervisor, admixtures may be used by the Contractor to assist in meeting the requirements of the Specification or to aid the placing of concrete.

Workability agents shall comply with MKS U.M1.035 and shall not have any adverse effect on the properties of the concrete. If a reduction in strength of the concrete is caused, the Contractor shall counteract this by a reduction in water cement ratio or by an increase in cement content.

Admixtures for watertight concrete

Powdered or liquid admixtures for achieving of concrete watertightness shall be used for all water retaining structures, pools and water reservoirs, chambers foundations and foundation slabs, structures exposed to frost and chemical aggressions and for damp proofing. The usage of this admixture shall be used  only with full particulars submitted by Contractor including chemical constituents of the admixture and the additional trial mixes mentioned above have been carried out and all are considered satisfactory.

Mixing with the concrete shall be in accordance to the manufacturer’s instructions.

The following requirements shall be satisfied in preparation of watertight concrete:

- The quality of the aggregate shall confirm with the standards for concrete and this specification;

- The minimal participation of particles less than 0.2mm together with the cement shall be 420 kg/m3 concrete mixture. Admixture shall be free of chlorides. Mixing with the concrete shall be accordance to the manufacturer’s instructions. During application using of vibrators shall be obligatory.

### 1.3.5 Transport of concrete

The concrete shall be discharged from the mixer and transported to the Works by means which shall prevent adulteration, segregation or loss of ingredients, and which shall ensure that the concrete is of the required workability.

The time elapsing between mixing and placing a batch of concrete shall be as short as possible, and in any case no longer as will permit completion of placing and compaction before the beginning of initial set. If the placing of any batch of concrete is delayed beyond this period, the concrete shall not be placed in the permanent Works.

### 1.3.6 Placing of concrete

Concrete shall not be placed in any part of the permanent Works until the Supervisor consent has been given in writing, and the Contractor shall give the Supervisor at least 18 hours notice of his intention to place concrete.

If concrete placing is not commenced within 24 hours of the Supervisor Representative's consent, the Contractor shall again request written consent as specified above.

(a) Preparation of surfaces to receive concrete

Any flow of water into an excavation shall be diverted through proper side drains to a sump, or be removed by other suitable methods which will avoid washing away the freshly deposited concrete or any of its constituents. Any under-drains constructed for this purpose shall be completely grouted up when they are no longer required by a method agreed by the Supervisor.

(b) Placing procedures

The concrete shall be deposited as nearly as possible in its final position. It shall be placed so as to avoid segregation of the concrete and displacement of the reinforcement, other embedded items (steel anchors), or formwork. It shall be brought up in layers approximately parallel to the construction joint planes and not exceeding 500 mm in compacted thickness unless otherwise permitted or directed by the Supervisor, but the layers shall not be less than four times the maximum nominal size of aggregate in thickness.

All the concrete in a single bay or pour shall be placed as a continuous operation. It shall be carefully worked round all obstructions, irregularities in the foundations and the like so that all parts are completely full of compacted concrete with no segregation or honeycombing.  It shall also be carefully worked round and between water-stops, reinforcement, embedded steelwork and similar items which protrude above the surface of the completed pour.

When concrete is discharged above its place of final deposition, segregation shall be prevented by the use of chutes, down-pipes, baffles or other appropriate devices.

### 1.3.7 Compaction of concrete

The concrete shall be fully compacted throughout the full extent of the placed layer. It shall be thoroughly worked against the formwork and around any reinforcement and other embedded items, without displacing them. Particular care shall be taken at arises and other confined spaces.

Concrete shall be compacted with the assistance of mechanical immersion vibrators, unless the Supervisor’s Representative agrees with another method. Immersion vibrators shall operate at a frequency of between 7000 and 10000 cycles per minute. The Contractor shall ensure that vibrators are operated at pressures and voltages not less than those recommended by the manufacturer in order that the compaction effort is not reduced. A sufficient number of vibrators shall be operated to enable the entire quantity of concrete ½ being placed to be vibrated for the necessary period and, in addition, stand-by vibrators shall be available for instant use at each place where concrete is being placed.

Vibration shall be continued at each point until the concrete ceases to contract, a thin layer of mortar has appeared on the surface and air bubbles have ceased to appear. Vibrators shall not be used to move concrete laterally and shall be withdrawn slowly to prevent the formation of voids.

Vibration shall not be applied by way of reinforcement nor shall vibrators be allowed to touch reinforcement or other embedded items. The vibrators shall be inserted vertically into the concrete to penetrate the layer underneath at regular spacing which shall not exceed the distance from the vibrator over which vibration is visibly effective.

### 1.3.8 Curing of concrete

Concrete shall be protected during the first stage of hardening from loss of moisture and from the development of temperature differentials within the concrete sufficient to cause cracking. The methods used for curing shall not cause damage of any kind to the concrete.

Curing shall be continued for as long as may be necessary to achieve the above objectives, but in any case for at least fourteen days. The curing process shall commence as soon as the concrete is hard enough to resist damage from the process.

Details of the Contractor's proposals for curing concrete shall be submitted to the Supervisor before the placing of concrete commences in the permanent Works.

### 1.3.9 Cement Screeds

The cement screed is a mix of cement, fine aggregate granulation (0-4 mm) and water.

The hardness of the cement screed shall be obtained by adding glass reinforcing fibres to the mix during its preparation. The minimum strength of the screed shall be 20 MPa and 30 MPa for industrial floor finishing.

The screed shall be levelled in two levels in case for different floor finishings.

The cement screed shall be compact and homogenous along its area avoiding so any poor mechanical characteristics.

The screed is ready to further application (ceramic tile, …) after about 28 days. For fast screed drying a special drying devices shall be used.

The min quantity of left humidity of the screed, using the CM method measuring with a tolerance of 0.1%, is:

- 3,0 % for ceramic tile

- 1,8 % for resilient floors

The max difference of the screed height along a 2 m length shall be less than 2 mm.

## 1.4. REINFORCEMENT

Reference: EN 10080, Eurocode 2; Eurocode 8

All reinforcement shall comply with the standard MKS C.K6.020 for deformed bars. For all structural elements, reinforcement shall be RA 400/500 steel with a characteristic yield strength fyd=400 MPa and a characteristic tensile strength of ftk= 500 MPa. Only ribbed bars shall be used.

All reinforcement shall be certified as free from radioactivity.

Welded Wire Fabric: Shall be electrically welded steel wire fabric for concrete reinforcement unless otherwise indicated on the drawings

Tie Wires: Shall be 1.2 millimeters in diameter, black annealed wire

The minimum concrete reinforcement cover shall be - Sides and bottom of footings cast against the earth (50+25)= 75 mm

All reinforcement for use in the Permanent Works shall be tested for compliance with the appropriate MKS standard in a laboratory acceptable to the Supervisor’s Representative and two copies of each test certificate shall be supplied to the Supervisor. The frequency of testing shall be as set out in the MKS standard.

Reinforcement shall be stored on Site either in racks or on a hard impermeable base so that it remains straight and free from contamination.

Reinforcement shall be securely fixed in position within a dimensional tolerance of 20 mm in any direction parallel to a concrete face and within a tolerance of 5 mm at right angles to a face, provided that the cover is not thereby decreased below the minimum.

All intersecting bars shall be tied together with a 1.6 mm diameter soft annealed iron wire and the ends of the wire turned into the body of the concrete, or shall be secured with a wire clip.

Proprietary spacers shall be used for ensuring that the correct cover is maintained on the reinforcement.

Spacers shall be as small as practicable and of a shape agreed by the Supervisor and designed so that they will not overturn or be displaced when the concrete is placed. Spacer blocks of mortar shall not be permitted in the permanent Works.

Before concrete is placed in any section of the permanent Works, which includes reinforcement, the reinforcement shall be completely clean and free from all contamination including concrete, which may have been deposited on it from previous operations.

## 1.5. METAL WORKS

The 1st class quality coating with following composition of phosphorus (P) and silicium (Si):

Si+2,5P<0,05%.

With the following mechanical properties:

|  | Tensile strength, Rm, MPa (N/mm2) | 0,2% Yield strength, Rp0, 2min, (MPa) | Brinell hardness, HB max |
| --- | --- | --- | --- |
| ### S235 | 360 – 510 | 235 | 100 – 154 |
| ### S275 | 370 – 530 | 275 | 121 – 163 |

## 1.6. MASONRY

### 1.6.1 Mortar

Reference: MKS U.M2.010 - Standard for quality of mortar for brickwork.

Mortar shall be composed of fine aggregate and type of cement. The mix proportions shall be as stated in the Bill of Quantities shall be one part of cement - two parts of lime and 6 parts of fine aggregate by weight.

Small quantities of mortar may be hand mixed but for amounts over 0.5 m3 a mechanical mixer shall be used.

The water content of the mortar shall be as low as possible consistent with the use for which it is required but in any case the water/cement ratio shall not be more than 0.5.

### 1.6.2. Walls of bricks and ceramic blocks (hollow)

Reference: MKS B.D1.015 - Standard for quality of hollow blocks made of clay

All the necessary material for brickwork shall be always in sufficient quantity. The necessary scaffolding shall be mounted in time.

The brickwork must be clean and with symmetrical connections. Joints shall be well covered with mortar, lines must be completely horizontal, and the mortar in the joints shall not be thicker than 1 cm. The built parts shall be vertical, as well as the edges and all visible surfaces on the wall.

Bricks and hollow blocks shall be dry, well baked, without lime and saltpeter, symmetrical form and edges without broken surfaces. All shall be in accordance with the current regulations.

The Contractor shall pay special attention to the block connections so the connective surfaces of the blocks shall be well filled with mortar.

In order to form symmetrical connections, blocks with special format shall be used in the process of brickwork to avoid breaking of the blocks.

The blocks that would be used in the brickwork, must be manufactured by a factory, with completely regular format, i.e. with all the necessary dimensions and proved quality.

1.6.3. Walls of stone

Mortar shall be composed of fine aggregate and type of cement. The mix proportions shall be as stated in the Bill of Quantities shall be one part of cement - two parts  fine aggregate by weight. Small quantities of mortar may be hand mixed but for amounts over 0.5 m3 a mechanical mixer shall be used.

The water content of the mortar shall be as low as possible consistent with the use for which it is required but in any case the water/cement ratio shall not be more than 0.5.

The stone shall be with the same quality as existing one.

## 1.7. SANDWICH PANNELS AND TINSMITH WORKS

Reference:

DIN ISO 4590 0.023EN 13163, Thermal insulation products for buildings; EN 1602 Rigid Cellular Certified "Fire-Resistant" Polyisocyanurate (PIR) foam

Verification of Conditions:

Before installing insulation, ensure that all areas that will be in contact with the insulation are dry and free of projections which could cause voids, compressed insulation, or punctured vapour retarders. Material used for thermal and acoustic insulation shall be of a high quality, non-combustibility, resistant to aging and resistant to humidity.

1.7.1 The installation of the rigid PUR panels should include all necessary installation accessories as:

Fasteners, stainless steel screws up to and including corrosion class C4. External flashing fastenings and panel washers, snow fences, ridge guards, walkways, and roof and vertical ladders. Bargeboard with angled gable flashing underneath with sill flashing externally and internally. Corner flashing, ridge capping, fill-in insulation strip between the two panels, interior ridge plate, eaves profile, front flashing, sill flashing long side, gable flashing, corner flashing, base cover flashing exterior, base cover flashing interior, sill flashing interior, sill flashing gable, case flashing, drip flashing, sill ledge, sill runner, 1.5 mm galvanized slotted U-profile.

10 cm thick facade/roof coated steel sheets, with PIR (polyisocyanurate) thermal insulaltion.The facade sandwich panel, in the f adade side, is corrugated sheet , thickness 1,5 mm. Core material density 30-45 kg/m3.

The panel should consist of the following layers:

- Final polyester coating acc. to RAL 9002

- Base polyester coating of 25 µ

- Galvanized (min 200 g/m2) plasticised steel sheet 0.3-0.8 mm thick, according to standard EN 10169 or plasticized alumina sheet 0.7 – 0.8 mm thick according to standard EN 485.

- Polyester coating

- Polyisocyanurate (PIR) foam

- Polyester coating

- Galvanized plasticised steel sheet 0.3-0.8 mm thick according to standard EN 10169 or plasticized alumina sheet 0.7 – 0.8 mm thick according to standard EN 485

- Base polyester coating

The technical data of PIR(Polyisocyanurate) core

| Enclose Rate: | 97% |
| --- | --- |
| Fireproof Rate: | B |
| Water Absorption Percent: | ≤1% |
| Thermal Conductivity: | ≤0.023 W/m·k |
| Temperature Range: | -185°C to +120°C |
| Bond Strength: | ≥0.09 MPa |
| Compressive Strength: | ≥0.22 MPa |

The dimensions, weight & thermal performance

| Core Thickness (mm) | 100 |
| --- | --- |
| U-Value (W/m²K) | 0.18 |
| R-Value (K/m²W) | 5.56 |
| Weight kg/m² 0.5/0.4 Steel | 12.2 |

### 1.7.2. Steel sheet gutters

Provide rainwater gutters, in pre-painted steel sheet 0.70mm, according to the design drawings, with su1.7.

### 1.7.3 Rainwater outlets

Provide rainwater outlet in pre-painted steel sheet 0.70mm or PVC market standard type, according to the design drawings. Outlet material shall be highly rust proof in any case.

### 1.7.4 Rainwater down pipes:

Provide and fix: rainwater down pipes round plastic film coated steel sheet 8/10 thick, fixed to the building walls with proper galvanized steel fasteners and steel clamps. The 3,00 m terminal at bottom will be crash proof cast iron made or heavy steel pipe made.

Final finishing: plastic film coated, with RAL in accordance with the facade treatment and Supervisor’s approval.

All the elements made of steel sections must be constructed according to the enclosed details, schemes, descriptions or Bill of Quantities and etc. They must be cleaned from all oil stains, covered with primary anticorrosive coating and then painted with appropriate enamel paint in two coats. Steel quality C0361. Testing of the steel profiles and welding shall be submitted to the Supervisor for approval before assembling in facility, transport and site assembly.

1.7.5. Flashing and covers

Provide and fix shaped flashing and covers, made in pre painted steel sheet, as ALUCOBOND or similar product. Alucobond is a light aluminum composite material consisting of two aluminum cover sheets and a core material made of polyethylene. Alucobond panels with impressive strength-to-weight ratio, energy efficiency, protects building interior from heating in the summer, protects against cooling and loss of heat in the winter and provides sustainability.

MATERIAL COMPOSITION

4 mm total nominal thickness, including proprietary fire retardant core

- The minimum bending radius without routing the interior skin is 15 times the thickness

- The minimum bending radius for 4mm without routing the back skin is 4”

- Withstands environmental temperature changes from -50oC to +80oC.

- Coefficient of linear expansion governed by the aluminum sheet

### 1.8. INSULATION WORKS

1.8.1. Synthetic membrane FLAGON SR

Reference: EN 1504-2, 1504-3, 1504-7; EN ISO 14001:2004

Composed of flexible PVC and a polyester reinforcement with  Resistance to wind stress, High resistance to weathering and ultraviolet rays, High mechanical resistance, Insensitivity to the hot-cold cycles, Resistance to puncturing.

Material data:

| Thickness (mm) | 1,50 | EN 1849-2 |
| --- | --- | --- |
| Weight (kg/m2) | 1,80 | EN 1849-2 |
| Tensile strength (N/5cm) | ≥ 1100 | EN 12311-2 |
| Elongation to break (%) | ≥ 15 | EN 12311-2 |
| Tear resistance (N) | ≥ 200 | EN 12310-2 |
| Resistance to impact (mm) | ≥ 800 | EN 12691 |
| Cold bending (°C) | ≤ - 25 | EN 495-5 |
| Hydrostatic pressure resistance (6 hours at 0,5 Mpa) | waterproof | EN 1928 met. B |
| Dimensional stability after 6 hours at 80°C (%) | ≤ 0,5 | EN 1107-2 |
| Resistance to artificial weathering (UV) | no surface cracking | EN 1297 |
| Resistance to roots penetration | no penetration | EN 13948 |
| Resistance to static punching (kg) | ≥ 20 | EN 12730 |
| Fire resistance | E | EN ISO 11925-1; EN 13501 |

1.8.2. 	Glass wool insulation

Glass mineral wool with long fibres, density of  45kg/m3,   thermal conductivity λ of  0039 W/mK (EN 126670), vapour conductivity  μ (acc. to EN 120861, air flow resistance (acc. EN 29053) > 5 kPa•s/m2, reaction to fire, Euroclass EN 13501-1A1, sound energy absorbent, max operating temperature of 230 ° C.,  melting point around  700°C., high material elasticity, high tension strength resistant to mechanical damage during the excecution manipulation.

    - Polystyrene insulation (EPS)

Thermal conductivity at 10˚C / 20˚C: λd= 0,0310 / 0,0325 W/mK

Thermal resistance at 10˚C / 20˚C: Rd= 1,61 / 1,54 m2K/W

Strength  (up to 10% deformation): 95 KPa

Flexure strength: 195 KPa

Elongation strength (normal to sides): 208 KPa

Resistance to vapour difusion: µ = 57

Water absorption  (48 hours): 0,054 kg/m2

Water  absorption  (7 дена): 0,64 %

Size dimensions  (48 hours at 70 ± 2˚C): 0,30 / 0,32 / 0,27

    - Lap jointed Extruded Polystyrene Board (XPS)

Reference: ISO 9001:2015 Quality Management System, an ISO 14001:2015 Environmental Management System, an ISO 50001 Energy Management System

Density: 38kg/m3

Weight/m2: 1.9 kg

Thermal Conductivity: 0.034W/mK

R-Value: 1.5m2K/W

Compressive Strength: 500 kPa

Water vapour resistivity: 750MN.s/g.m

- Excellent thermal conductivity,

- High compressive strength,

- Highly resistant to water absorption,

- Long term dimensional stability

- Service temperature limit up to +70oC,

- Certified Green Guide rating of A,

- Zero Ozone Depletion Potential and a Global Warming Potential < 5,

1.8.5. Waterproofing

Reference: EN 1504-2: 2.2(C); 8.2(C

On walls and floors shall be applied flexible cementitious waterproofing system in 3 layers, on the top of the floor cement screed laid to falls and cement-sand plastered walls, crack-free up to designed  height of the walls. Each subsequent layer is applied upon a previously dried out layer. The overall thickness of all three layers approximately 1.5 to 2.0 mm. Complete as per drawings, specifications and manufacturer’s recommendation subject to Supervisor’s approval. Waterproofing shall be subject to test for a 100 mm water height kept for a period of 48 hours. Before to be applied first layer substrate shall be treated with U-bond, or similar approved.

The surfaces treated with cement based additive shall be protected from direct sunlight, wind and low temperatures for the first 7 days. Mixing of components and application shall comply with manufacturer’s instructions.

Characteristics

Density of mixed material:  МКС EN 1015-6 1,14-1,26 g/cm³

Fresh mixed material consistency:  МКС EN 1015-3 240±20mm

Adhesion: EN 1542 ≥0,8 MPa

Adhesion in case of thermal conditions (frozing /defrozing cycles):EN 13687-3 ≥0,8 (0,5) MPa

Vapor conductivity: EN ISO 7783-1 SD<5m - class I

Capilary absorpsion and water conductivity: EN 1062-3 w<0,1kg/m² h0.5

Rupture elongation at 20°С - 15%

Fire reaction: EN 13501-1 F

Implementation temperature: 10-35˚С

Workability:  3-4h

Dryness time at 20˚С

Surface: 2-3h

Complete dryness: 24-48 h

1.8.6. PVC sheet waterproofing

Reference: EN 13956

Mechanical characteristics at -35oC to +110oC.

Straigthness:	EN 1848-2 = <= 50 mm

Flatness EN 1848-2: <= 10 mm

Dimensional stability EN 11077-2:  max 0.3%

Max tensile force EN 12311-2: >= 1000 N/50 mm

Elongation at max tensile force:  >=15%

Tear resistance (EN 12310-2: >= 180 N

Joint shear resistance EN 12317-2: >= 900 N/50 mm

Reaction to fire EN 13501-1: Class E

Impact resistance EN12691: 1250 mm

Factor  EN1931: 150004500

1.9. DRY WALL AND CEILING WORKS

Ref.: DIN 18180-GKB, EN520-Type A

1.9.1 Gypsum boards to walls for sound absorption including air-cleaning effect as a linear ceiling panel that has a surrounding stepped edge for precise laying without joint filling, as well as a brilliant white paper on the visible face for direct cladding. Panels are laid with butt joints.

Specification

- Material: Gypsum material, Zeolite

- Thickness:12.5mm.

- Dimensions: 120cm X 200cm.

- Edge Details: UFF.

- Appearance: black/white rear board liner and an ivory/white colored face board liner.

- Sound absorption.

- Air-cleaning effect.

- Pollutant reduction.

- Sound absorbing properties.

- Brilliant white paper on the visible surface.

- Continuous holes, edge formation 4FF (2 each as tongue and groove) with edges primed and chamfered at the factory.

Comprises grid system made up of main runners and cross tees that are suspended from the structural deck with rod and clips for levelling. Systems are manufactured from cold rolled, formed, galvanized mild steel.

Framing Grid- Furring/Lower Channel Configuration: CD50/27/0.6mm channels spaced at 600 mm, max 100mm from existing ceiling;

Perimeter Channel Configuration: UD28/27/0.6mm channels fixed to perimeter

Anchoring to Basic Ceiling - Steel dowel or approved anchors

1.9.2. Suspended ceiling

Suspended ceiling  comprises grid system made up of main runners and cross tees that are suspended from the structural deck with rod and clips for levelling. Systems are manufactured from cold rolled, formed, galvanized mild steel.

Framing Grid- Furring/Lower Channel Configuration: CD50/27/0.6mm channels spaced at 600 mm, max 100mm from existing ceiling;

Perimeter Channel Configuration: UD28/27/0.6mm channels fixed to perimeter

Anchoring to Basic Ceiling - Steel dowel or approved anchors

Suspension System - 4 mm thick hanger wires attached to structural soffit

Load Class of Suspender: 25 kg;

Spacing of Suspender: 50 mm;

Max. Allowable Ceiling Drop: 100 mm;

1 Board arrangement

Always place linear notch edge adjacent to linear lap edge along front and long edges. Align and fix reference cord in the middle of the room in the direction of the application. Align first board row along reference cord and fasten boards. Apply following board rows acc. to manufacturer installation scheme - 1st board row, start application in the middle of the room.

2 Fastening of boards (drywall screws)

Fasten Acoustic linear Boards with Drywall Screws SN 3.5x30 on metal grid made of CD 60x27 channels. Screw spacing is 170 mm. Press the boards firmly on to the grid during screw attachment. Commence fastening in the corner, where the board is already bordering a board on the long and front side. Fasten the long side first and then the front side

Paint coats: Silicate-based emulsion paints may be used after referring to the manufacturer’s recommendations for priming of the respective surface.

Finishing - Taped and jointed for a seamless finish. All work of other trades above the ceiling shall be completed prior to the start of the ceilings. Mechanical, electrical, thermal insulation and other trades shall make available to the ceiling contractor, prior to the start of the ceiling installation, adequate descriptive literature, samples and shop drawings of any item that is to be carried by or fixed to the ceiling.

# 2. CRAFTSMEN WORKS

## 2.1. FINISHING WORKS

### FLOOR FINISHING WORKS

      - Industruial Floor

Dry coat on the base of  cement and minerals as quartz, granite and corrund. With high resistance to wearing, high impact strength, high physical and mechanical loads , final finishing with mechanical device application, non- sleepage floor, susceptible to curling and cracking using the largest possible aggregate and lowest water content possible. Allowed wetness of the base max. 3-4% to concrete C25/30 screed. The concrete screed base shall be treated/prepared appropriately.

Materials used for industrial floor execution:

| Base | Comsumption, kg/m2 | Impact strength MPa | Resistant to abrasion | Hardness acc. to Moss scale |
| --- | --- | --- | --- | --- |
| Quartz | 4-5 | 60-75 | 6-8 | 7 |
| Granite | 4-5 | 75-85 | 4-6 | 8 |
| Corrund | 4-6 | 85-95 | 2-4 | 9 |

## Site Preparation & Placement Environment

All concrete slabs on ground require good subbgrade or base beneath to support the concrete. But note that the critical thing is uniform support. The base material should be compactable, easy to trim, granular fill that will remain stable and support construction traffic. To test this, perform proof rolling on a grid pattern for the entire slab area.

#### 2.1.1.2 Floor ceramic tiling

Reference: UNI EN 87; UNI EN ISO 10545

Floor tiles shall be first class with matt glazed finish and abrasion resistant. The Contractor shall provide firm and flat base prior to apply the floor tiles.

The tiling of the floor surfaces is carried out horizontally without waves, with flat surfaces or with appropriate slope, with uniformed and equal closed joints.

Supply and installation of floor porcelain tiles th = 10 mm - The tiles are placed on adhesive on previously dried cement screed or leveled surface. Filling the tiles with 1 mm joint with a joint mass, it is obligatory to leave the dilatation between the wall and the tile, which is filled with silicone. When execution of the tiles on the cement screed, always connect the tile joint to the dilatation joint of the screed, so that there will be no cracking in the tiles due to the work of the screed dilatation. If you change the width of the floor surface sharply (crossing one in another room, space constraints), or expansion of the lateral space, the joint always should be performed with a joint.

Skirting tiles, 100 mm high, shall be fixed securely to the walls with an adhesive recommended by the manufacturer.

2.1.1.3 Raised Modular anti-statoc floor

PANELLS 60/60CM, FROM MOULDED GALVANIZED STEEL SHEETS FILLED WITH CEMENT COMPOUND, COVERED WITH ANTISTATIC PVC-FLOOR TYPE "П2"

Raised anti-static floor from heavy loaded metal panels 60/60cm, H=60cm

Specifications of panels:

- Dimension of panel 60/60cm, panel weight 50 kg/m2

- 35mm deep with no covering

- All steel welded construction filled internally with a cementitious core material

- Full hard cold rolled steel top sheet

- Protected from corrosion by an epoxy paint finish

- Class A flame spread rating

- Non-combustible material

*Understructure options :

60cm heavy duty bolted stringer w/8ga. Fillet welded heads

*Covering options : tile factory laminated with HPL, or covered with heterogenous PVC layer d=2mm

*System Performance Criteria :

-Static loads : design loads 907kg, Ultimate loads min. 1814kg, safety factor min.2

- Rolling loads: 10 passes-680kg, 10000 passes-567kg

- Impact loads: 91kg

## 2.1.2 WALL FINISHING WORKS

##### 2.1.2.1. Ceramic work to walls

Tiles shall be of first class quality and they shall satisfy the standards for tiling interior of public premises Reference: UNI EN 87; UNI EN ISO 10545.

The tiles shall be with sharp and right-angled edges. The Contractor shall submit a sample to the Supervisor and shall approve the quality of the tiles.

The lining of wall surfaces shall be carried out very precisely, in a flat and vertical manner, without waves, bulges and depressions; they shall have uniformed and equal wide joints.

The horizontal joints continue along the whole perimeter of all the walls in the same room, while the vertical ones must be constructed at a plumb bob, regardless the way of lining; i.e. whether the walls are lined in a form of alternating joints or “joints over joints”.

The ceramic tiles could be installed in two different ways: either with cement mortar or with adhesive for wall or floor tiles.

After the tiling, joints shall be processed with an appropriate sealing compound.

The wall surfaces shall be flat, smooth, firm and clean prior tiles to be applied.

Wall surfaces must be vertical, while the points where two walls are connected must be at a right angle (90) unless the design itself does not anticipate something else.

The walls must be prepared on that way so they could be lined with ceramic tiles and thickness of a coat of 6-8 mm, depending on the thickness of the tiles and the adhesive coat.  All inner and outer angles shall be lined with rounded plastic or metal edge strip.

Supplying & fixing of porcelain stoneware (Gres) wall tiles of 8 mm thick, glazed surface finishing of required shade, laid over adhesive  with closed joints, absolutely in line and flush, grouted with tile grout to match the tile and cleaning the surface. Complete as indicated on the drawings, to the approval of the Supervisor, and according to manufacturer's recommendations.

##### 2.1.2.2. Painting

Reference: EN 13300 UNI EN 10795

The material used for paint works shall be of top quality and the works shall be done properly to the satisfaction of the Supervisor.

For all types of paint works, the base shall be cleaned of dust and all kinds of dirtiness such as resin, oil, grease, rust, cement, bitumen and etc. The painting is allowed only on dry and ready surfaces. Prior to applying of paint all walls and ceilings, which shall to receive paint, shall be skimmed and smoothed.

Skimming shall be smooth and flat with thickness differences and precision less than 2 mm measured in horizontal, vertical and diagonal directions of the skimmed walls.

After the painting has been accomplished, there shall not be any traces of paintbrushes or rollers on the painted surfaces. The paint (tone) shall be with equal intensity and without stains at whole surface of the wall.

Emulsion water based paint shall be applied for interior use. Existing painted ceilings and walls shall be prepared and clean (sanding the surfaces and repairing existing cracks and holes), painting with one undercoat made of tinted emulsion water based primer and two (2) coats of tinted emulsion water based paint Complete as indicated on the drawings, to the approval of the Supervisor, and according to manufacturer's recommendations.

Emulsion water based paint, formulated for interior use shall be applied to already plastered walls and gypsum boards. Prepare and clean surfaces (sanding the surfaces), smoothening with two (2) coats of adequate putty filler, painting with one undercoat made of tinted emulsion water based primer and two (2) coats of tinted emulsion water based paint.

Smoothening of interior walls

Procurement of material, skimming of interior partition walls with proper compound for this kind of wall. All unevenness has to be levelled with abrasive paper. Surfaces shall be painted with dispersive paint in two coatings, colour and shade as per Supervisors choice.

Painting of gipsum board ceilings, internal walls

Procurement of material, fairing and painting gypsum plasterboards surfaces. Boards joints screw holes have to be dry and without dust. All unevenness has to be levelled with abrasive paper. Surfaces shall be painted with dispersive paint in two coatings, colour and shade as per Supervisors choice.

  - BLACKSMITH WORKS

Reference EN 10219 (cold formed hollow sections); EN 10210 (hollow sectional properties); EN 287 (Approval for welders); EN 10021 (testing steel)

2.2.1	Floor greed

Channel covering grate made from steel profiles cold and hollow steel profiles.

The works covered under this section consist of fabrication, supplying and installing in position steel structural elements in accordance with drawings and subject to the Supervisor approval.

All the elements made of steel sections must be constructed according to the enclosed details, schemes, descriptions and etc. They must be cleaned from all oil stains, covered with primaryanticorrosive coating, and then painted with appropriate enamel paint in two coats Materials shall be new and of first class quality, free from defects and imperfections and shall fulfil the designated classifications.

Generally, steel quality shall be S235JRG2 (Č 0361) with minimum yield strength of 235 MPa(EN 10025:1993) or equal, except for bolts, 8.8 (DIN 931) hot dip galvanised and painted after assembly in accordance with 00/03/TS001.

(1) Fabrication and design shall be according to the appropriate provisions of EN 1993-1-1.

(2) Fabrication shall in general aim to minimise welding on site. Welding on site should only be carried out in exceptional cases.

Welding and Weld Tests

- Preparation

(1) Members to be joined may be cut to shape and size by mechanical means such as shearing, machining, and grinding or by gas or arc cutting, to suit the conditions. Edges shall be shaped to DIN 8551. Selection of filler materials shall be in accordance with approved standards and shall allow thorough penetration and good fusion of the weld with the filler material.

(2) The edges of surfaces to be welded shall be sound metal, free of visible defects such as laminations or defects caused by cutting operations, at least 30 mm back from the edge of the weld, and also free from rust, oil, grease and other foreign matter.

- Performance

(1) Operators who have been previously qualified by test according to EN 287-1 to perform the type of welding in question shall perform welding.

(2) All welding shall be in strict accordance with the design details as to type, size, technique and sequence.

(3) The Contractor shall prepare and submit a welding program for all welding according to EN 288-2. The welding program shall define all welds by location, define shaping, welding

method, weld types, welding directions and weld rod or wire type. Tests of certain weld

procedures may be requested.

-Quality and testing

(1) Welding quality shall be according to EN ISO 5817, character C, and control of welding by

independent or approved laboratory.

Surface Treatment and Painting

The surface treatment and painting of all structural steelwork shall be in accordance with EN ISO 12944.

Preparation of steel substrates before application of paints shall be by methods such as blastcleaning, hand and power tool cleaning getting free the presence of rust and mill scale, the presence of surface contaminants, including salts, dust, oils and greases (ISO 8501). Before start applying first coat of primer at workshop, the Supervisor shall inspect and carry out visual assessment of surface cleanliness and consent it.

Based on the corrosivity category and the expected durability in accordance with EN ISO 12944 anticorrosive paint systems are given as follow:

Shall be used air-drying alkyd paints (oxidative curing).

-Primer rust proofing alkyd, one coat at shop, min. 80 μm dry-film thickness and at site over all welds shall be applied second coat before start applies of finishing enamel alkyd coats.

-Finishing enamel alkyd paint, (oil-synthetic enamel) for metal surfaces, two coats, min. 2x80 μm total dry-film thickness. Colour to be sampled and submitted to the Supervisor for approval. First coat of paint shall be lighter than second coat, for recognition purpose.

2.2.2 Tempered glass fence

Constructed from premium quality, toughened safety glass that is 10 mm thick, 100 cm high with safe, polished bevel edges, in using framed glass systems that utilize a handrail attached to posts ensuring a guardrail in place should the glass shatter.

Glass panels must be heated to very high temperatures and then immediately undergo rapid cooling to become tempered. All glass used for rails must be tempered and shatter resistant. Edges should be finished and polished. Installation shall be installed to already executed floor on/to aluminium profile posts/supports. The profile is closed with decorative strips.

2.3. EXTERNAL DOORS AND WINDOWS

2.3.1 Aluminium profiles (aloy of AlMgSi acc. To EN AW 6060) for windows and doors with general profile thickness 1.4 mm with anodizing protectiion of 12 microns and powder thickness of 100 microns.

. Frame depth  50 mm
. Leaf depth 57 mm
. Leaf bearing device ≥ 130 kg

. Hardness – 70 HB

. Profile thickness – 1.8-5 mm
. Glass thickness 4 mm
. Insulation - 18mm poliamide  - EN ISO 10077-2 Uf=2,9 W/m2K

. Air penetration - EN 12207 - Class 4
. Impermeableness - EN 12208 - Class 9A
. Resistance to wind pressure - EN 12210 - Class C5

. Geometry profile control – EN 12020-2

. Three levels of ERDM gaskets, class C

The aluminium profile surface shall be protected by plastification with previously droping the profile in NaOH solutionand priming with chromium oxide. Finaly a positive electricized paint powder is applied by special difusors and polemirized in oven on 180-200oC forming a plastisized layer of  50 - 70 µ.

The glass is low emission insulating filled in with argon 90.

2.4 INTERNAL DOORS AND WINDOWS

2.4.1 Aluminium profiles for windows and doors with general profile thickness 1.4 mm with anodizing protectiion of 12 microns and powder thickness of 100 microns.

. Frame depth  50 mm
. Leaf depth 57 mm
. Leaf bearing device ≥ 130 kg

. Hardness – 70 HB

. Profile thickness – 1.8-5 mm
. insulation – cardboard honeycomb Uf=2,9 W/m2K

. Geometry profile control – EN 12020-2

. Three levels of ERDM gaskets, class C

2.4.2 Aluminium profiles for windows and doors with general profile thickness 1.4 mm with anodizing protectiion of 12 microns and powder thickness of 100 microns.

. Frame depth  50 mm
. Leaf depth 57 mm
. Leaf bearing device ≥ 130 kg

. Hardness – 70 HB

. Profile thickness – 1.8-5 mm
. Glass thickness 4 mm Uf=2,9 W/m2K

. Insulation - 18mm poliamide  - EN ISO 10077-2 Uf=2,9 W/m2K

. Geometry profile control – EN 12020-2

. Three levels of ERDM gaskets, class C

      - Gaskets

Only integrated, or profile manufacturer recommended type of internal, external gaskets, or other ancillary profiles shall be installed, in order to guarantee that the specified performance of the windows are met in respect of closing gaps on the contact areas and preventing air infiltration.

Material used for gaskets shall be EPDM to comply with a temperature range from -20oC to +700C

      - Hardware

Hinges, locks, handles, keeps, screws shall provide stabile and long lasting use of windows. Hardware shall be fixed to frame and sash, fastened to the steel reinforcement. Hardware and multi locking mechanisms to be manufactured according to EN 12209:2003. Handles, locking systems and hinges to be manufactured of steel or alloy, resistant to corrosion and durable in regard to surface finishing.

      - Glazing works

The glass should be transparent, colourless, without waves and bubbles. The glass panes shall be of the type and thickness specified in the item. Their sizes shall be as shown in the drawings. The glass panes shall be of quality and make approved by the Supervisor. They shall have properly squared corners and straight edges. Damaged or defective glass shall be replaced with new glass at no additional cost. Each piece of glass shall be delivered with factory labels intact, indicating glass type, quality and thickness. Labels shall not be removed until installation has been accepted.

Setting block shall be of neoprene of rubber width and high enough to provide minimum edges clearance for glass. Protect glass from breakages immediately upon installation by applying suitable warning markings.

Windows and external doors shall be glazed with thermal insulating double panes 4+16+4 mm, space filled with dry air (argon), Ug˂0,6W/m²K, outer pane coated reflective (silver).

All glasses in doors with double or single pane shall be tempered.

### 2.5. FAÇADE WORKS

### 2.5.1 Stone wall

The stone piece shall have height and length accordingly to existing stone wall façade. The rule for execution of the stone wall is similar to the execution of brick walls. The stone shall be, if necessary, appropriately by carving. At each 120-150 cm of height the wall shall be labelled through all its depth. The joints are filled in with mortar to avoid any penetration of water in the wall. The stone lining shall be minimum 20 cm thick.

2.5.2 Stone wall cleaning out

First cleaning out procedure for the cleaning treatment of the stone shall be a mechanical cleaning as dry/wet sand blasting using appropriate device exterminating dirty layers, traces.

The stone surface could be cleaned out using dry-treat solution by brush and strong alkali cleaner with oxygen. The solution shall act about 15 minutes with brushing and washing the surface with water jet.

The cleaning out shall be avoided under strong sun.

    - External louvres

Provide 95% protection against sun thermal energy and 99% protection against UV rays. The louvers shall be adjusted accordingly depending on sun rays direction.

Louvres are made from extruded 1.6 mm thick aluminium curved sheet with polyurethane filling. The louvres shall be positioned manualy or automatically using corresponding device by 220 V motor with clip with tilting transmission to the lever connected with louvre. All louvres are moved under same angle avoiding any overlapping.

The aluminium surface shall be coated with powder coating acc. to RAL as a microstructure or by anodization. The aluminium louvres shall be installed under appropriate angle.

Standards and characteristics:

- Standardi i karakteristike sistema:

- Profile chemical composition:	EN-AW66 T66

- Profileshape tolerance: 		EN 12020 – 2.

- Size tolerance:			 DIN 17615

- Extrusion technological way:	 DIN 1748

- Statics:				DIN 1055

- Surface treatment:		DIN 17611

- Quality control:			DIN EN ISO 9001

3. LIFT

Reference MKC EN 81-41 for lifts, and EU Machinery Directive 2006/42 /EEC.

3.1. Enclosed vertical platform lift

With ready-made modular concept, designated for the persons with impaired mobility (wheelchair users), with the following basic features:

Control devices: Hold to run drive (dead-man grip buttons) on the control panel and automatic drive on the landing call buttons according to the essential safety requirements of the Machinery Directive 2006/42/EG.

The lift shall be equipped with emergency lowering system by battery, activated in case of power failure. To emergency lower the lift pushing any landing button inside the lift will take the lift down. Emergency lowering is also featured from the outside of the lift. A battery surveillance system will monitor the battery capacity.

Shaft: A prefabricated shaft with shaft panels in steel. Corner profiles and panel frames in anodized aluminum. The shaft is fast and easy to install, without welding. Shaft Ceiling with LED lights. Inclined roof for outdoor lifts included. Reinforced fixing brackets will secure the outdoor lift to the building.

Platform: The ergonomic design of the platform control panel includes extra-large push buttons with hold-to-run operation, in compliance with MD 2006/42/EC. Telephone equipment, emergency stop and alarm button shall be included. The alarm signal can be connected through to an external emergency call center. The platform shall be equipped with safety edges on all four sides. Lifting of platform with screw-driven system with electric motor.

- Location: Indoor

- Load capacity: 400 kg;

- Travel speed: min 0.15 m/sec

- Number of stations/entrances: 2 stops;

- Travel height: H=3.25 m;

- Platform size (width x length): 900x1400 mm; (Bujar da proveri)

- Driving system: Screw-driven with electric motor

- Rated motor power / Power supply: max 2-2.5 KW / 230V-AC

- Prefabricated shaft size (w×d):1469x1509mm;

- Max. number of stops: 2;

- Shaft: Steel panels- off white RAL 9016;

- Door configuration: single-entry / open through;

- Doors type: swing doors;

- Doors material / model: steel with panoramic glazing;

- Clear door opening sizes (w×h): 900/2070 mm;

- Control system: microcomputer based system;

- Shaft Ceiling with LED lights;

- Roof inclined for outdoor lifts;

- Auto LED lighting on platform;

3.2 Testing and Commissioning of Lifts

Testing shall be performed by certified/authorized inspection company in conformity with Macedonian Rulebook for using lifts (Official gazette 26/2009) and EN 81.1. After passing satisfactory test, shall be issued a Technical Report for commissioning lifts in use.

# 4. INSTALLATIONS WORKS

# 4.1. WATER SUPPLY, FIRE PROTECTION and WASTE WATER

## General

This specification covers the material and equipment required for the complete systems and the general methods of installing the materials and equipment. Sections of the work covered by this specification shall include the following:

Cold and Hot Water Supply Installations

Waste Drainage Installation

Fire Protection Installation

This specification shall be followed in comply with the Drawings, the Bill of Quantities and other Contract Documents as well as standards МКS EN.

The Contractor shall check the existence of any surface or sub-surface structure in the surrounding area of his work. He shall not disturb or damage any of these structures and shall make necessary provisions by shoring or other means necessary to avoid damaging these structures. Any damage shall be immediately repaired at the expense of the Contractor.

All workmanship shall be of the highest standard in every respect and shall be performed only by skilled mechanics, recognized as such in their respective trades.

## Water Supply

The existing connection of  110 mm shall be used. A new water supply and firefighting network realized as a ring along the boundary of the lot shall be executed.

The building water supply and firefighting protection shall be realized with a connection of  100 mm from the existing water supply connection. The outdoor water supply networks shall be executed under the ground laid out in a layer of 10 cm thick sand at a trench 80 cm wide and 130 cm deep.

The available pressure at the connection point is expected to be 3 bars. The water supply of the whole complex shall be realized from the city water supply network.

16 garden hydrants are designed in the scope of the ring network along the lot boundary used for the green areas of the lot watering.

The consumed water amount shall be measured by a water counter unit in a water measuring manhole.

The sewage network is designed to receive all waste waters from the toilets and floor inlets to the sewage manholes. The sewage pipes shall be of hPVC with a minimum diameter of  50 mm and highest diameter of  110 mm. The horizontal gradient of the sewage pipes, laid in the building floor slab, is from 1% to 3%. The manhole is close to building with PVC pipe  110 mm connection. The manhole capacity shall be 40 Mp.

Firefighting hydrants networks

According to the Official Gazette of the Republic of Macedonia No 26-2018.

The available pressure at the point of connection to the city water supply network is 3 bars. In the scope of the hydro technical conditions for the water supply of the building with a fire fighting water supply it shall be realized by the city water supply network. The proscribed amount of water for firefighting is 5 l/s and the necessary pressure in the ring water supply network is 3 bars. The pipelines are dimensioned by tables with a coefficient of roughness of n=0,0012.

The indoor hydrant distribution is by galvanized pipes.

A ring distribution is conceived around the building by polyethylene pipe  110 mm with 8 over ground hydrants in the scope of the regulation line.

The installation testing shall be under a pressure 50% higher than the operational one in the presence of the Supervisor. The installation shall be measured and checked out at the most lower point with a calibrated manometer. The installation completed, it shall be checked out in relation to its reliability and functionality. After that a chlorination of the lines shall be realized as well as a water analysis.

Toilet equipment

The equipment in the toilets (WC pan, basin, pissoirs, showers shall be from white faience and nickel plated fixtures. The accessories equipment as connection devices, WC pan seat, etc. shall be same in the building.

### 4.1.1-1. Polypropylene PPR pipes

PP-R pipes should be manufactured in accordance with MKS ISO 15874 (1,2,3): 2014 or equivalent. The material PP-R polypropylene is stable at low temperatures, up to -35°C. Working pressure PN min 10 bar. To have a certificate of potable water issued by accredited laboratories

#### 4.1.1-2. Polyethylene PE pipes and hoses

PE pipes and hoses should be made of PEHD materials and satisfy the following plastic quality: MKS EN ISO 12162: 2011 or equivalent. PE-100 hoses and tubes shall be made according to MKS EN 12201-2: 2011 + A1: 2014 or equivalent, which is identical to EN 12201-2: 2011 + A1: 2013 or equivalent. To be used for drinking water according to: DVGW W320 or equivalent, DVGW GW335 - TeiLA2 or equivalent. Internally, they have a white layer with resistance to the accumulation of plaques.

The electrofusion fittings must be made conventionally with the technology of injection of polyethylene, exclusively PE 100 or equivalent. All fittings comply with the requirements of MKS EN 12201-1: 2014 or equivalent. The electrofusion fittings must be packed in transparent protective bags, on which the manufacturer's name, product description, product drawing and relevant dimension and quality will be indicated. Wiring for heating the fitting should be completely attached to the body of the fitting and fully covered with a thin layer of polyethylene in order to avoid exposure to dirt, dust and soil. The fixing device (screws) must be part of the fitting up to the dimension of 63 mm. in order to better connect the surface of the fitting and the pipe in the case of the presence of irregularity on the tube itself. The barcode containing all the necessary information for automatic welding must be affixed with waterproof paper on the fitting. The barcode must have the ability to monitor. Process voltage must be fixed to min. 40 V. The terminal pins must be at most 4 mm. in diameter. All electrofusion fittings must have fusion indicators, mandatory in cone shape in order to avoid the escape of melted PE material during the fusion process. The maximum welding power of the fittings should not exceed 4 KWA

### 4.1.2. Galvanized tubes

To be according to MKS EN 10255 + A1: 2009 or equivalent, (galvanized according to MKS EN 10240: 2009 or equivalent with external thread on both sides according to MKS EN 10226-1: 2009 or equivalent

### 4.1.3. Ductile pipes with standard joints certified for potable water

The pipes should be made of Ductile Iron with length L = min. 6m and working pressure min PN16bar

• The coupling should be on the muff using a standard rubber made of EPDM (certified for drinking water).

Muff should be protruding on the outer rim for more efficient installation of a repellent ring for the muff.

• Inner tubes should be coated with a cement layer (centrifugally applied to the inside of the pipe) produced by potable water in accordance with European Directives 98/83 / CE according to MKS EN 197-1: 2012 or equivalent (to be provided with a certificate from an accredited laboratory )

• The outer tubes should be coated with a Zn-Zinc and Al-Aluminum coating layer with a minimum thickness of 400 g/m2 (in the ratio of min. 85% Zn - Zinc and Al - Aluminum residue) applied evenly over the entire external surface of the tube .

• The product should have a DVGW quality certificate or equivalent

The pipes should comply with the following standards:

Specification and test methods: MKS EN 545: 2010 or equivalent

Cement internal protective layer: MKS EN 545: 2010 or equivalent

Outdoor protective layer of Zn-Zinc and Al-Aluminum MKS EN 545: 2010 or equivalent

Standard bonding rubber (EPDM material) MKS EN 681-1: 2006 / A3: 2008 or equivalent (to have a certificate from an accredited laboratory). The tire, i.e. the whole connection should be tested together with the pipes (to have a certificate from an accredited laboratory). The products shall be examined in an accredited laboratory in accordance with MKS EN ISO / IEC 17025: 2006 or equivalent

### 4.1.4. Testing the pipeline

All tubes should be tested for hydrostatic pressure and for each tube a Certificate should be issued.

Prior to receiving and putting the pipeline in use, it must be tested at internal pressure.

The examination will be carried out in accordance with the existing legislation and standards. The methodology for testing pipelines is different depending on whether it is a pressure pipe, drainage pipes or sewage pipes, in accordance with the applicable test method. The same should be done by experts and supervised by the Supervisor.

### 4.1.5. Hydromechanical equipment

#### 4.1.5.1 Galvanized fittings

To comply with MKS EN 10242: 2009 or equivalent. The brass valves shall comply with MKS EN 1074-1: 2010 or equivalent. The valves will be used in the water supply system. Internal thread according to MKS EN 10226-1: 2009 or equivalently. Working pressure min 16 bar.

Ball valves shall be made of Brass P-OT 58 Pb 2 according to MKS EN 1074-1: 2010 or equivalent. Internal thread according to MKS EN 10226-1: 2009 or equivalent. Operating pressure min 30 bar

#### 4.1.5.2 Fittings and connection elements

The fitting shall be made of ductile iron according to MKS EN 545: 2010 or equivalent. The nominal pressure min. PN10 requires. To have internal and external epoxy protection min. 250 microns. The fitting is in accordance with the following standards, specification and test methods; MKS EN 545: 2010 or equivalent. MKS ISO 2531: 2010 or equivalent, made from ductile iron EN GJS 400-15 or equivalent. Flanges should be made according to: MKS EN 1092-2: 2009 or equivalent.

#### 4.1.5.3. Adapter couplings with a wide range of tolerances for elastic coupling of various pipe types

Adapter couplings with a wide range of tolerances for elastic bonding of various pipe types in dimensions from DN50mm to DN300mm to be made from ductile iron according to standard MKS EN 1563: 2012 or equivalent, to be manufactured according to standard MKS EN 14525: 2009 or equivalent. Adapter couplings shall be made for working pressure of minimum PN16bar, to have EPDM rubber sealing rubber (antibacterial rubber) which is made according to standard MKS EN 681-1: 2006 / A3: 2008 or equivalent.

Anticorrosive protection should be done by applying material that will not endanger the health of people. The corrosion protection of the adapter joints is confirmed by a document for health correctness issued by an accredited laboratory according to standard MKS EN ISO / IEC 17025: 2006 or equivalent, in accordance with the applicable - Food Safety Law and the Rulebook on the General Requirements for Safety of Materials and Products to Come in contact with food. The permitted angular deviation (deflection) of the adapter connectors is min. min. 6 ° two-sided. Adapter with flange with wide range of tolerances for elastic bonding of various types of pipes in dimensions from DN350mm to DN600mm to be made of hot rolled structural steel according to standard MKS EN 10025-2: 2009 or equivalent. Flange adapter to be manufactured according to standard MKC EN 14525: 2009 or equivalent.

The dimensions of the flanges shall be according to standard MKS EN 1092-1 + A1: 2013 / AC: 2014 or equivalent. Adapter flanges to be made for operating pressure of minimum PN16 bar, to have EPDM rubber sealant (antibacterial rubber) made according to standard MKS EN 681-1: 2006 / A3: 2008 or equivalent. The anti-corrosive protection of the flange adapter shall be performed by applying material that will not endanger the health of the people and it is confirmed by a document for health correctness issued by an accredited laboratory according to standard MKS EN ISO / IEC 17025: 2006 or equivalent, in accordance with the applicable law food safety and the Rulebook on the general requirements for the safety of materials and products coming into contact with food. The permitted angular deflection (deflection) of the flange adapter must be min. 3 ° unilaterally.

Adapter couplings with solid-state fixing couplings for PE / PVC pipes made of ductile iron according to standard MKS EN 1563: 2012 or equivalent, with double О ring made of EPDM material according to standard MKS EN 681-1: 2006 / A3: 2008 или equivalent and steel safety toothed protection ring. To have an integrated stretch protection ring, teflonized steel screws and nuts. Anticorrosive protection from thermoplastic polymer Rilsan nylon 11. Working pressure PN16.

EN 1563: 2012 or equivalent equivalent double duct O ring made of EPDM material according to standard MKS EN 681-1: 2006 / A3: MKS EN 1563: 2012 or equivalent, with double O ring made of EPDM material according to standard MKS EN 681-1: 2006 / A3: 2008 or an equivalent and steel safety toothed collision ring. To have an integrated stretch protection ring, teflonized steel screws and nuts. Anticorrosive protection from Rilsan nylon thermoplastic polymer 11. The dimensions of the flanges to be in accordance with standard MKS EN 1092-2: 2009 or equivalent. Working pressure PN16.

#### 4.1.5.4. Fire-fighting underground hydrants

The underground fire extinguishers shall be fitted with a double closing system in accordance with MKS EN 1074-1 or equivalent, according to DVGW or equivalent registered for drinking water. The hydrant shall possess the following characteristics: Automatic shut-off system using a ball. Double exit system with two independent leakage lines with high-pressure protection on the water and a water retention system after closing. The hydrant has a secure system for keying the joints of the main valve. The hydrant has a self-winding claw that is constantly adjustable turn off to the open position. The chassis has retaining nuts with integrated protection of the opening, the spindle is closed. Integrated multi-function sealing of the flange for connection. The fuse according to MKS EN 1092-2: 2009 or equivalent. Body, hat and cloth made cast iron EN GJS 450-10 or equivalent. Crown water armature of ductile iron EN GJS 450-10 or equivalent, completely vulcanized with EPDM rubber. Internally and externally coated with epoxy protection of min.250 microns in accordance with GSK regulation. Spindle is made of inox steel min. class 304. All nuts and bolts must be made of stainless steel EN 1.4301 or equivalent. The main pipe and the connection pins shall be made of stainless steel EN 1.4301 or equivalent. The spindle and valve assembly shall be made of brass.

#### 4.1.5.5. Pressure relief valves

Pressure regulating valves to be automatic control valves for pressure reduction with a special by-pass for lowering the pressure and at low flow rates. The automatic pressure relief valve is diaphragmatic and consists of:

1. Main valve 
2. Pilot circuit (insulating ball valves, central control unit, appropriate pilot valves depending on the function to be performed by the main valve, position indicator on the main valve with built-in air vent for ventilation, inlet and outlet pressure gauge, inlet and outlet manometers); special by-pass for low flow pressure reduction.

The automatic control valve should be in accordance with the following standards:

Integrated length: MKS EN558 + A1: 2012; MKS ISO 5752: 2010 or equivalent

Flanges to be made according to MKS EN1092-2: 2009 or equivalent

Hydraulic test according to: MKS EN 12266-1: 2012; MKS ISO 5208: 2010 or equivalent

The automatic control valve must be made of:

Body and cover: Ductile iron GJS 400-15 (GGG40) or equivalent; Protection: Internal and external epoxy protection min. 250 microns in accordance with GSK regulation or equivalent.

Pilot circuit: The pipes of the pilot circuit are made of stainless steel

Indicator: Indicator of the position of the main valve with venting valve

Membrane: nylon anchoring rubber or equivalent.

Cover cover: stainless steel min. AISI 302 or equivalent.

Nuts and washers: stainless steel min. AISI 303 or equivalent.

Saddle Rubber: Nitril (NBR) - Rubber according to MKS ISO 4658: 2010 or equivalent.

Retention ring: stainless steel min. AISI 316 or equivalent.

Strap: stainless steel min. AISI 303 or equivalent.

Body saddle: AISI 316 stainless steel or equivalent.

Quad-ring sealant sealant with anti-vibration shape, manufactured according to American standard AS 568 or equivalent

The central control unit itself contains: Regulation of the opening speed, regulation of the shutter speed, regulation of the reaction speed of the Automatic Control Valve and filter for the pilot circuit. To be made for operating pressure of minimum pressure PN16 bar.

#### 4.1.5.6. Service valve for building connections

Non-return valves for horizontal piping shall be made of ductile iron GJS 400-15 (GGG40) according to standard MKS EN 1074-3: 2010 or equivalent, length according to MKS EN558 + A1: 2012 or equivalent. Flanges are made according to MKS EN 1092-2: 2009 or equivalent. Awning made of stainless steel. A ductile iron disk protected by a vulcanized EPDM according to MKS EN 681-1: 2006 / A3: 2008 or equivalent, to be approved and possess a hygienic certificate issued by an accredited laboratory. The anti-corrosion protection of non-return valves (externally and internally) should be performed by applying an epoxy coating. Anticorrosive protection of irreversible valves is confirmed by a document issued by an accredited laboratory. Non-return valves shall be designed for minimum operating pressure of PN16 bar.

#### 4.1.5.7 Rubber flange gaskets

The flange gaskets to be made of NBR material shall be made according to standard MKS EN 681-1: 2006 / A3: 2008 or equivalent, which is identical to EN 681-1: 1996 / A3: 2005 or equivalent. The rubber flanges for flanges shall be certified by a health certificate issued by an accredited laboratory according to standard MKS EN ISO / IEC 17025: 2006 or equivalent, in accordance with the Law on Food Safety and the Rulebook on the general requirements for the safety of materials and products coming in contact with food. Working pressure min PN16 bar.

The technical board (rubber seal) is for general purpose and used for sealing places between water and air. Its composition is made of SBR material, with a thickness of min. 5 mm and min. 3 canvas. The surface of the technical board (rubber seal) is smooth. The technical plate (rubber seal) is confirmed by a health certificate issued by an accredited laboratory according to standard MKS EN ISO / IEC 17025: 2006 or equivalent, in accordance with the applicable Law of Safety food and the Rulebook on the general requirements for the safety of materials and products that come into contact with food.

### 4.1.5.8. Protection of water lines

Water lines shall be protected from contamination and disinfected with chlorine. The water line shall be sterilized after all tests and cleaning of the lines have been performed as described hereinafter.

Cold and hot water lines shall be thoroughly disinfected with a solution containing not less than 50 parts per million of available chlorine, whether liquid chlorine or calcium hypochlorite or chlorinated lime. The solution shall be introduced into the lines in an approved manner. The sterilizing solution shall be allowed to remain in the lines for 8 hours during which time all valves and faucets shall be opened and closed several times.

After sterilization, the solution shall be flushed from the lines with clean water until the residual chlorine content is not greater than 0.2 part per million, unless otherwise directed.

### 4.1.5.9. Electric water heaters for hot sanitary water

The thermal storage electric water heater shall be of the pressure thermostatically controlled type. The heater shall consist of a copper or glass lined steel pressure vessel with foam polyurethane insulation and stove enamelled sheet metal casing. The inner pressure vessel shall have a design pressure of 10 bar. The heater shall be controlled by an adjustable thermostat and protected by a high limit cut-out thermostat with manual reset button. It shall have an isolating valve and not return valve on the cold water feed. The heater shall have inlet and outlet connections and single phase element. It shall be suitable for floor mounting.

The size and power rating of the heater shall be as specified in the Bill of Quantities. Heating element capacity shall be 1 KW for 10 l and 2 kW for 50 l.

### 4.1.5.10. Water flow meter

The Contractor shall provide and install water flow meter of approved type, with dimensions specified on the Drawings or in the Bill of Quantities. Water flow meters shall comply with ISO 4064/1. The Contractor shall submit, for approval, to the Supervisor all information regarding the performances of the equipment he intends to install.

### 4.1.5.11. Fire cabinets

Fire cabinets shall be in accordance with the detailed contract Drawings and the Bill of Quantities. The Supervisor shall approve a sample of the cabinets, prior to the installation. Cabinets shall be wall recessed type, made of th=1 mm thick galvanized steel sheet, painted with epoxy-polyester powder coating, at least 80 µm thick, red color RAL3000 and with lock and lever (Yale or Euro type) including all necessary fittings and supports. Cabinet shall consist following parts:

- Synthetic fire hose, 15 m length along with hose reel

- Water jet DN 52 mm with quick shut-off handle.

- Angle stop valve 2"

### 4.1.5.12. Testing and commissioning

The pipe-work shall be tested as the work proceeds. When a section of pipe-work is completed it shall be plugged and then it shall be slowly and carefully charged with water, allowing all air to escape and avoiding all shock or water hammer. The pipe-work to each room shall be tested individually and each riser shall also be tested individually.

The Supervisor’s Representative shall attend every test and the tests shall be repeated until the Supervisor’s Representative is satisfied. The test shall be to a pressure not less than 1.5 times the working pressure of the system. The pressure shall be maintained for minimum 24 hours.

The whole installation of hot and cold water services and fire protection shall be tested on completion of the work prior to handing over. The pipe-work shall be slowly and carefully charged with water as described above.

All piping fittings and appliances shall be checked as for satisfactory support and protection from damage and corrosion.

The piping system has to be subject to a pressure test in accordance with current MKS EN standards.

### 4.1.5.13. Sanitary Fixtures

All sanitary fixtures shall be installed in accordance with manufacturer’s instructions and as required to obtain a rigid installation. The location of each fixture and the fixing method of ceramic fixtures or stainless steel fixture shall be in accordance to current regulations.

After all fittings have been installed, ready for use and before completion, all fittings furnished and installed shall be thoroughly cleaned out leaving each and every part in perfect condition and ready for use.

Sanitary ware shall be as specified in the sanitary appliances schedule, Drawings or Bill of Quantities.

The sanitary equipment shall only be installed after the toilet or room has been plastered.

The Contractor shall take adequate precautions to ensure that the sanitary ware is not damaged in any way before or after installation. Any piece of sanitary ware that is damaged shall be replaced at the Contractor’s expense. The Contractor is responsible for handing over all sanitary ware in good condition. No damaged piece, by any reason, will be accepted.

4.1.5.14 Ceramic sanitary ware

The ceramic sanitary ware shall comply with MKS EN standards and to have less than 0.5% deviation in length, deviation in thickness less than 5%, straightness of side, surface flatness less than 0.5% , water absorption <3, hardness by Mohs >5, abrasion resistance, frost proof, shall have constant colour, chemical and thermal shock resistance, stain proof, shall not expand by changes of humidity, crazing resistance minimum 2 cycles.

Installation of porcelain WC pan shall be complete with a solid plastic lid and a low mounting cistern, including all fittings, all elements of first class quality for public buildings.

Installation of porcelain washbasins shall be fixed in a semi-boot wall and a one-way cold and hot water battery, first class for public buildings.

Installation of porcelain urinal shall be fixed type in the wall and single-hand battery

Installation of first-class sanitary accessories  shall be provided for public use. Mirror 60/70 cm, chrome toilet paper holder, chrome armrest paper holder, fixed stand to water closet of stainless steel, movable stand to water closet of stainless steel.

Floor siphon from ABC for pipe connection 50 mm with height of 70 mm with chrome cast iron cover

### 4.1.5.15. Testing of sanitary fixtures

Prior to handing over the structure to the owner, each piece of sanitary ware shall be tested. Each water closet shall be flushed twice and checked for leaks and any other defects by the Supervisor’s Representative.

Each basin and washstand shall be filled to the overflow level and then after running the water through the overflow for a minimum of 30 seconds the plug shall be removed. The Supervisor’s Representative shall inspect each of the above-mentioned fixtures for leaks and defects.

Any defects or leaks shall be repaired or in the case defect being ships or cracks or other visible damage, the fixture shall be replaced at the Contractor’s expense. Any sanitary ware refused by the Supervisor for any other reason shall be replaced at the Contractor's expense.

## 4.2. Waste Drainage Installation

### 4.2.1 Piping

Pipes shall be run in straight lines and have a uniform gradient as the table hereinafter, except  where such gradient on overhead pipes would reduce the headroom materially, the gradient may be reduced if so directed and/or approved by the Supervisor’s Representative or shown on the Drawings.

| Pipe Size | Percentage |
| --- | --- |
| 50 mm. and less | 2% |
| 75 mm. and more | 1 1/4% |
| 110 mm. and more | 1% |

Waste pipes shall be set at the correct distance from the face of the floor or wall to ensure a good joint with the fixture piping.

Piping shall be kept free from scale and dirt. Pipes shall not be split, bent, flattened, nor otherwise injured either before or during the installation. No bend or curve shall be made in any pipe, which will reduce the waterway or alter the internal diameter of the pipe in any part.

All cutting shall be square to the pipe axis by approved means and all burrs removed. The use of pipe cutting machines, which reduces the bore of the pipe, shall not be permitted.

All pipes shall be free from culls, dents or other surface damage. At the time of final inspections damaged pipe shall be removed and replaced with new pipe.

Where practicable, pipe-work shall be carried out as the structure proceeds so as to minimize the amount of cutting away and repairing.

The run and arrangement of all pipes shall be as shown on the Drawings and as directed during installation. They shall be as straight and direct as possible, forming right angles or parallel lines with structure walls and other pipes and be neatly spaced.

All ends of pipes shall temporarily plugged to prevent dirt accumulating.

Rainwater shall not be drained into sewers intended for sanitary sewage only.

### 4.2.2 Piping and Fittings Materials

PVC pipes and PVC fittings should be made of solid polyvinyl chloride PVC type 100 (CM). PVC Tubes should be with a class of rigidity min SN4 according to MKS EN ISO 9969 or equivalent. PVC Tubes should be in accordance with MKS EN 1401-1: 2011 or equivalent. PVC pipes to be delivered with a length of min 3m to max 6m

All indoor pipes & fittings shall be made of unplasticized polyvinyl chloride (PVC-U) conforming to EN 1329-1(Plastics piping systems for soil and waste discharge (low and high temperature) within the building structure).

All outdoor pipes & fittings shall be made of polyvinyl chloride (PVC-U) conforming to EN 1401-1(Plastic piping systems for non-pressure underground drainage and sewerage outside building).

### 4.2.3. Ventilating

Ventilating pipes shall go through walls or roofs to vent into the open air, at the points shown on the Drawings. The ventilating pipes shall be fitted with a galvanized steel sheet cover at the top.

All vent and branch vent pipes shall be so graded and connected as to drip back to the waste pipe by gravity. The vent pipe shall rise vertically or at an angle not more than 45 degrees from the vertical, to a point at least 150 mm. above the flood level rim of the fixture it is venting before offsetting horizontally or before connecting to the branch vent.

### 4.2.4 Flashings

Pipes extending through roofs shall be flashed with sheet lead, copper or other durable material to make the roof watertight.

Complete Drawings showing method of flashing as may be required by the Supervisor shall be submitted for his approval prior to the installation.

### 4.2.5 Manhole cover with a circular shape

A manhole cover with a round-shaped frame in accordance with EN 124, load class D 400. The lid and frame must be made of ductile iron and with adequate anti-corrosion protection. The lid must be connected to the frame on one side of the hinge, and on the other side by means of a key for locking with a key and a keyhole integrated with the construction. Dynamic stability must be provided at least through three contact points. The contact surface between the lid and the frame must have a ring of composite material for vertical stabilization. The construction must ensure that the cover is at least 130°C and blockage of the 90° cover for protecting employees from sudden closing

### 4.2.6 Testing and commissioning

Entire drainage system shall be tested for water tightness and smoke tightness during and after completion of the installation. No portion of the system shall remain untested. Contractor must have adequate number of expandable rubber bellow plugs, manometers, smoke testing machines, pipe and fitting work tests.

All materials obtained and used on site must have manufacturer’s hydraulic test certificate for each batch of materials used on the site.

Before use at site all pipes shall be tested by filling up with water for at least 30 minutes. After filling, pipes shall be struck with a hammer and inspected for blow holes and cracks. All defective pipes shall be rejected and removed from the site within 48 hours.  All openings and connections shall be suitably plugged as approved by the Supervisor. The total head in the stack shall be 4.5 m at the highest point of the section under test. The period of test shall be min for 30 minutes. If any leakage is visible, the defective part of the work shall be cut out and made good.

On completion of the work the entire installation shall be tested by smoke testing machine. The test shall be conducted after the plumbing fixtures are installed and all traps have water  seal or by plugging the outlets with bellow plugs.

## 4.2 ELECTRICAL INSTALATIONS WORKS

GENERAL

Whenever local regulations, local standards (MKS), or any common practice of trade, are subject to any interpretation, clarification, ambiguity, or dispute, a ruling by the Supervisor shall prevail, always provided that such ruling shall be fully in compliance with, and shall be based on the subject local regulations, local standards (MKS), as well as in accordance with common practice of trade.

All works must be carried out precisely and professionally. Prior to application, the Supervisor must examine all material and all his comments referring to material and quality of work shall be obligatory for the Contractor. The agreed prices include all fully completed works, the final product, and ready for use.

The Contractor shall be responsible for any and all damages caused by the Contractor during any works, to any third party, structure, main building or adjacent buildings, and any and all repair works and compensations of any kind shall be at the Contractor’s expense

Upon completion of the works, the Contractor shall be liable to carry out all specified tests and measurements and submit written certificates in the form of attest to the Supervisor.

TECHNICAL CONDITIONS, STANDARDS AND REGULATIONS

Standards and regulations

Complete electrical installation should be in accordance with existing laws, rules and regulations:

- Latest version of the Construction Law in Republic of North Macedonia

- Valid regulations for electro-technical installations

- IEC 60364 Electrical installations for Buildings

- IEC 60947-2 Low-voltage switchgear and control gear

- IEC 61439-1/2 Low-voltage switchgear and control gear

- IEC 60269-1/2 Low-voltage fuses

- EVN rules of power engagement

- International standards

  - International Electro technical Commission Publications (IEC)

  - International Organization for Standardization Publications (ISO)

  - European Norms prepared by European Committee for Electro technical Standardization or European Committee for Electro technical Commission Publications (EN)

9.Requirements derived from fire-fighting service

Electric Power Cable Installation Lying

Cable installation lying is not recommended if outside temperature is lower than - 5 C, or, cables shall be previously heated and laid as soon as possible.

Prior to commencement cable laying, the Contractor shall be liable to verify if drum is not secured (cable ends are not closed in factory) or cable is cut for voltage test; to close cable ends accordingly, immediately upon completion of tests; to inspect entire trench and check if it is ready for cable laying. During cable acceptance on drum, it is necessary to remove attest on factory testing from drum and check the data and compare them with drum plate. If there is no attest, voltage test shall be conducted on cable.

Power cables are laid into earth, water, and ducts, on piers, over bridges and similar. Cable run shall be selected to fulfil optimal Engineering and economic conditions and be in compliance with existing underground installations, along with approval of competent land development authority. Lying of cables is carried out manually or mechanically, where permissible bending semi-diameters and allowed traction forces shall be observed. Permissible bending semi diameters for 1 kV cables with PVC insulation are 12D (external cable diameter. Use of sheaves for spreading is recommended on hardly accessible or dangerous places (slide of land or other materials). It is forbidden to spread cables using motor vehicle, towing on ground, cable braiding (twisting), cable throwing into trench, rupture or bending over permissible limit. Upon cable laying and prior to filling of routing (run), competent survey authority should carry out cable run survey. Ends of laid cable should be designated using plates containing basic data on cable and designation of cable run (routing). It is recommended direct laying of power cables into ground, into cable trench, which depth and width depend on cable nominal voltage, soil type, number of cables laid in the trench and intersection with other underground installations.

A usual and common depth of cable digging into soil is 0.7-0.8 m for cables. Deviations are allowed on smaller lengths regarding intersection with other installations and in case of unfavourable laying conditions (rocky soil). As for road and street crossing, digging depth should be 1m for all voltage levels. usually performed drill under way.

Common cable bedding procedure onto 20cm sand or fine-grained excavation earth shall be applied for the first layer next to cable. Mechanical protection made of 2 mm thick plastic shield shall be placed above laid cables and red warning plastic strip "CAUTION ELECTRIC POWER CABLE” shall be placed at 0.4 m further above cables.

Approaching or intersecting with other underground installations shall be dealt and described separately for each type of installations:

In case of approaching and intersecting with water supply and sewage system; (i) at places of intersection, water supply and sewage system pipes can be laid beneath or above power cable. Vertical spacing at place of intersection must be at least 5 m, and if cable is protected from mechanical damages using concrete or iron pipes 1m each from both sides, spacing at place of intersection should be at least 1m; (ii) parallel laying of power cables is not allowed above or beneath water supply or sewage pipes; (iii) parallel laying of power cables and pipes for water supply and sewage system is allowed in horizontal plane, where horizontal spacing must be larger than 0.5 m, and if cable is protected from mechanical damages using concrete or iron pipes, spacing should be larger than 0.25 m; (iv) trench excavation for parallel run and at places of intersection must be carried out manually without mechanical means in order to prevent cable damage.

In case of approaching and intersecting with heated-water pipeline: (i) at places of intersection, pipes of heated-water pipeline are laid above power cable, where vertical spacing must be larger than 0.5 m for 1 kV cables; (ii) intersection must not be carried out in heated-water pipeline ducts and manholes; (iii) parallel laying of power cables is not allowed above and beneath of pipes for hot-water pipeline; (iv) parallel laying of power cables and pipes for heated-water pipeline is allowed in horizontal plane, where horizontal spacing must be larger than 0.5 m for 1 kV cables; (v) if it is not possible to observe the mentioned spacing, appropriate thermal protection shall be placed or cables with braided polyethylene insulation shall be laid at those places; (vi) trench excavation for parallel run (routing) and at places of intersection shall be carried out manually without mechanical means in order to prevent cable damage.

In case of approaching and intersecting with roads: (i) intersecting angle should be as closer to 90 as possible, and not lesser than 30; (ii) power cables should be laid in hard plastic PVC pipes for cable sewage system with 110 mm diameter. These pipes must be longer by 1m from external road edge and pipe ends shall be marked with standard cable designations; (iii) vertical spacing between upper road surface edge and power cable must be larger than 1m; (iv) as for approaching and parallel routing of power cables with roads, horizontal spacing from road surface edge must be larger than 1m.

In case of approaching and intersecting with telecommunication and IT cables: (i) intersecting angle should be as closer to 90 as possible, and not lesser than 45; (ii) power cables are laid beneath telecommunication cables at places of intersection, where vertical spacing must be larger than 0.3 m for 1 kV cables; (iii) approaching and parallel routing of power cables and telecommunication cables is allowed, where horizontal spacing must be larger than 0.3 m for 1 kV cables; (iv) if mentioned spacing cannot be achieved, then cables are placed into2-3 m long protective tubes, power cables into electric conducting tubes, and telecommunication cable in electric non-conducting tubes, where spacing must be higher than 0.3 m; (v) trench excavation for parallel routing and at places of intersection must be carried out manually without mechanical means in order to prevent cable damage.

In case of approaching and intersecting of power cables: (i) vertical spacing must be larger than 0.2 m at places of intersection for power cables, where lower voltage cables are laid above higher voltage cables; (ii) during parallel routing, horizontal spacing must be larger than 0.07 m.At the same trench, 1 kV cables and higher voltage cables, as well as higher voltage cables mutually, must be separated with line of bricks or other insulating material .In case of approaching to buildings, which connection for each separate building is covered under indoor installation section parallel routing for power cables near foundations or walls of buildings, that is, frontage (building) line must be at a distance of 0.5 m, and when there are more cables in trench, spacing should be not less than 0.3 m.

Telecommunication and IT Cable Installation Laying

Cables are generally laid from movable drum by unrolling. If cable is laid from an immovable drum cable rollers shall be used i.e. entailing of cables on the ground or on the bottom of the trench is not allowed. If for any reason using rollers is not possible cable may be laid manually provided however that the allowed load for workers is not exceeded (25 kg maximum) and cable must not be bent under minimum allowed bending diameter.

Cable is laid approximately at the middle of trench with reserve. During laying of several cables into the same trench, care should be taken that they do not intersect or overlap. At the points of cable lengths end an overlap of at least 1 ÷ 1,5 m is left in accordance with the guidelines of the manufacturer of the equipment and cables.

Cable bending curvatures in order to reach the extension shall be about 50% bigger than minimum allowed bending curvature in order to avoid radial forces.

Along with telephone cable, into the same trench without limitation the following cables may be laid:

  - Coaxial cables for TV cable distribution systems

  - Fibre optic cables for any purpose

Horizontal distance between telephone cable and power cable (including high power antenna feeder cables) shall be at least 50 cm. If the distance is less special protective measures shall be provided.

The angle of intersection of ТТ & IT cables and power cables shall be 90º and at least 45º. If angle is less, this is the case of parallel guiding. At the occasion of intersection ТТ and/or IT cable is always on top of the power cable with vertical distance of at least 30 cm for low voltage cables and 50 cm for high voltage cables.

Cables are at 5 m distances marked with lead clips with the following data written on them: (i) type of cable and construction; (ii) month and year of laying and (iii) number of the cable from the design i.e. the number given by the authorized TELEKOM department.

Common cable bedding procedure onto 20cm sand or fine-grained excavation earth shall be applied for the first layer next to cable. Mechanical protection made of 2 mm thick plastic shield shall be placed above laid cables (two parallel series if there are several cables). Approximately at the middle of the trench depth yellow warning strip with "CAUTION TELEKOM CABLE” written on it shall be placed.

Under the barriers: roads, railroads, embankments etc. hard plastic conduits of Ø125 mm inner diameter shall be placed. At least two parallel conduits shall be laid. Conduits are laid down into the layer of sand or concrete depending on the load. Minimum depth for installation conduits is 0,8 m between upper border of the conduits and surface level. Intersection with barriers is at the angle of 90º and minimum angle of intersection is 45º. Optical, TT, TV and/or any IT shall bi entered into building through previously mounted Ø110mm protection pipes and shall further be led to a building’s „Data rack“.

Execution of the external electric power supply system works, shall for each particular case include substantial portion of works, which have been specified elsewhere in this section Civil Engineering Works (93), such as:

Inserting cables through Cable Ducts:

- One cable only shall be inserted through one duct. Insertion of several cables through the same tube is allowed if total diameter of all cables does not exceed 60 mm. Fibre optic cables i.e. PE tubes for blowing in of fibre optic cables should be inserted through separate tubes. Splicing of cables in ducts is not allowed.

- Cables are inserted first through tubes of the lowest row – according to plan given in the design. In manholes cables are placed on consoles at lateral walls.

- Insertion of cables through several manholes without splicing is allowed if maximum pulling force specified for those cable types is not exceeded.

- Insertion of cables is done by manual or motor winch. Control of pulling force during cable insertion is obligatory. The best solution is when the winch is equipped with a friction clutch slipping through in case the pre-set pulling force exceeded.

- For reduction of friction in tubes lubricating materials may be used.

- Insertion of cables shall be done from the drums being distributed according to predefined arrangement given in work organization.

- Upon completion of cable insertion damaged and pulled sections shall be cut from cable ends. Care should be taken that enough spare cable is left for placing on the consoles of the manholes and for cable joint overlap.

LV equipment (230/400V)

Complete equipment shall provide continuous work in health facilities, with respect to the following conditions:

- 230/400V, 50Hz, TN-S

- Rated insulation voltage of 400V between two phases and 230V between phase and ground

- Voltage level deviation is given in specification and/or drawings

- Complete equipment should be designed to work shortly under industrial environment  with rated voltage of 6kV (1.2/50s)

- Complete material and equipment should be new, unpacked and protected from mechanical damages and weather conditions. All damages of the material during transportation or on-site is at responsibility and cost of Contractor.

- Contractor should submit technical documentation for complete material and equipment. Documentaiton should consist of all details needed for tender evaluation, including Manufacturer Authorization Form.

- User manual and instruction for maintenance. After completion of work, Contractor should provide User manual and instruction for maintenance.

Exclusion applies, where this is different with specification or drawings.

Labeling

Labeling shall be on Macedonian language and in accordance with drawings. Labels should be made of white plastic with black or red signs.

Equipment testing

Testing of electrical equipment shall be done in accordance with appropriate standards and recommended procedures by vendor.

Functional testing

Additionally, wider scope of testing with functional testing of operational electrical system should be performed.

Functional test of fixed electrical installation should be performed in order to confirm that electrical installation is ready to perform expected functions and operation.

All current circuits shall be confirmed by using operation of their break in order to ensure that current circuit is installed in accordance with design. Test should incorporate following activities:

- Turn on and off of lighting circuits in order to prove that lighting circuit correspond with switch, protective device and sign

- Turn off of main current circuits in order to prove that each circuit correspond with protective device and that protective device operate in accordance with designed functionality

- Turning off of main switch/contractor in order to prove that proper current circuit is controlled by main switch/contactor

- Turning off of all current circuits on all blocks to prove that insulation work properly

- Turning off of all selector switches to prove that chosen sequence is in accordance with designed

- To prove that protection devices respond accordingly with designed criteria

- Other tests as per vendor recommendations and requirements of the Contracting authority/Investor

Measurements and attest

After completion of electrical installations, following measurements shall be done by independent authorized company:

- Resistance of the grounding probes

- Insulation resistance of all circuits

- Time off

- Other measurements required by authorized bodies.

# Е.1 EXTERNAL ELECTRICAL INSTALLATION

## E 1.1 SITE PREPARATORY WORKS

All ancillary works (excavation, backfilling, etc.), necessary when relocating other installations, shall be considered as preliminary works that must be performed by the Contractor fully in compliance with the instruction of the Supervisor. Such work shall involve engagement of the work force and equipment, for excavation, transport and disposal of excavated material, fully observing provisions prescribed for transportation of surplus materials as defined under hereof.

## E 1.2 ALIGNMENT WORKS

Marking of trench excavation alignment

Prior to commencement of excavation works, Contractor is liable to make necessary centreline alignment setting of the trench / excavation, including all required elements, direction changes, manholes, connections, intersections and other structures.

Marking of existing installation

To bring the situation under obtained drafts underground cadastre, or if not received, proceed to the examination of alignment with individual hand-dug test ramps

E 1.4 EARTH AND CONSTRUCTION WORKS

Before excavation works, the Contractor shall undertake all necessary preparations and preliminary works, as described under section Е 1.1  above.

Prior to the commencement of the works, the Contractor shall propose organization of the work that must be approved by the Supervisor.

If the excavation is performed in the area of existing infrastructure (electric, communication, hydro technical, gas pipeline, etc.), and their routes are not for any reasons marked on the site, then it shall be necessary to determine the position of these installations before the commencement of any works. The location of such installations, if there is no any other way, shall be found by excavation of the pipeline (by cut grips). After determining the exact position of these installations, the Contractor shall make geodetic survey of installations and send the report to the competent organization in charge for maintenance of these installations. The Contractor must not start the excavation unless the Contractor is sure that the subject installation is “clean” as regards the existing installations. The Contractor shall be liable to compensate any damage incurred to these installations during excavation works.

The excavation works shall include securing and bracing of lateral excavation sides, as well as securing of the adjacent structures, which shall be made according to the land nature, that is, position of the adjacent structures, and all labour related to these activities shall be on Contractor’s expense. The Contractor shall be liable to proceed entirely according to the Geo-engineering Study.

Land surveying control and measurements necessary for excavation works must be made accurately and fully in compliance with the design. The costs for performance of all necessary surveying works shall not be separately calculated and paid. The Contractor shall include all these costs in the unit price. If there are any survey beacons on the route for excavation, the Contractor shall return them at his own expense into their original state.

Types of Excavations in respect of Underground Water

"Dry" excavation shall mean all excavations made above the groundwater table at the time of the excavation. In case of an eventual inflow equal, or less, than 3 l/sec per 50 m2 of an excavated surface, the Contractor shall drain excavation pit by use of sufficient capacity pumps, without any extra payment.

"Excavation beyond groundwater table" shall mean all excavations made beyond and/or at the groundwater table at the time of the excavation, or excavation in case on inflow higher than 3 l/sec per 50 m2 of the excavated surface. The Supervisor shall establish occurrence of an "excavation beyond groundwater table", and only then and during the period of time of such circumstances established by the Supervisor. In such cases ISO 14688-1, together with ISO 14688-2, shall apply, providing a general identification and description of soils based on a flexible system for immediate (field) use by experienced persons.

The nests and caverns between some categories of material, not exceeding 1 m3, shall not influence the classification of material and shall not be rejected or added to other categories.

Payment shall be made per unit prices for particular items of excavation. The price includes excavation, levelling and cleaning of the bottom and sides of the excavation, and in case of trenches with discarding of material (small particles and earth to one side and larger stones to another side of the trench), all required strutting and other means of supporting and protection of excavation, all required material for digging including insurance of traffic, crossings, etc.

The price of excavation, in case of “dry” excavation (as referred above), shall include pumping of trench water and/or ground water, rainwater and/or water of any other origin.

The Contractor shall cover compensations for devastated land and cultures, as well as for all other damages that may arise consequently, and shall pay all other costs that may occur due to excavation out of the borders defined in the Design.

#### Trench for Electric Installation

Route survey and excavation of trench, dimensions 0,7x1,2 m and 0,4x0,8 m, with obstructions in the free terrain, for  low and high voltage cables in the same horizontal plain at a distance of 50 cm from each other. Creating a beding for cables made of two layers of gravel, granulation 0-1 mm or  fine subsoil, layer thickness 10 cm each. Placing of PVC warning tape 40 cm above every cable, buffering of the trench in 30 cm layers with compacting with a mechanical compactor in two layers,  and transport of excess material.

E 1.5 MATERIALS FOR PROTECTION OF CABLES IN TRENCHES

Making sand layer under and around cables

In cohesive and solid soil clay, mild clay), in the rock or soil containing coarse gravel or stone, it is impossible to lay the pipe/cable directly on natural base since such soil cannot be shaped suitably. In such a case, it shall be necessary to make sand bedding.

After completed montage of pipes/cable and other trench accessories, the trench shall be backfilled around and above pipes/cables (except at pipe/cables connections) with 10-20 cm sand, applied in 10-20 cm hand compacted layers. If motorized rammers are used, subject to the Supervisor’s approval, the manufacturer’s instructions must be strictly observed.

Pipe connection spots shall be backfilled with 10-20 cm hand compacted sand layers upon successfully performed pressure testing, subject to the Supervisor’s approval.

PVC warning tape

A red plastic warning tape with the name "CAUTION HIGH VOLTAGE CABLE" should be placed at a height of 0.4 m above the LV and HV cable laid in the trench.

VC warning tape - yellow

A yellow plastic warning tape with the name "CAUTION LOW-CURRENT CABLES" should be placed at a height of 0.4 m above the cable TT and FO laid in the trench.

PVC gal shield

Mechanical protection for cables to be installed, from 2mm thickness and 1m length, PVC gal shields placed on LV, V/SN cables along the entire length.

#### Supply of PVC pipes ф 75mm and ф 100mm

Supply and installation of a PVC pipe Ф 75mm for mechanical protection of cables in a trench at crossings under the road, complete with jointed material and other shaped parts.

Supply and installation of a PVC pipe Ф 100 mm for mechanical protection of cables in a trench at crossings under the road, complete with jointed material and other shaped parts.

#### Supply of PVC conduit hose for cocrete ф 26mm

Supply and mounting of PVC halogen free conduit hose ф 26mm, for mounting in concrete wall in accordance with standard EN 50085-2-1.

### E.1.6 EARTHING INSTALLATION

| ICS number | Standard number | Year | Title |
| --- | --- | --- | --- |
| E 1 | MKS C.K5.030 | 1972 | Galvanized steel strips for earthing - Technical requirements for manufacture and delivery |

#### Supply of material and construction of earthing tape

Supply of material and construction of earthling tape, by means of  FeZn tape 30 x 4mm. hot deep galvanized  Leave vertical outlets, FeZn tapes 30x4mm, from the earthling tape, for connecting to street lighting pillar. Tape shall be laid in already excavated trench at 100% .

#### Cross piece tape-tape  60x60 mm

Supply of material and construction the cross piece tape –tape with dimension 60x60mm hot deep galvanized

#### Review and control of   installation

Review and control of   installation, measuring resistance of earthling on each test joint, issuing attestations and technical acceptance of completed works. included in position E 4.1.1

E 1.7 CABLES FOR EXTERNAL POWER DISTRIBUTION

| ICS number | Standard number | Year | Title |
| --- | --- | --- | --- |
| E 1 | EN 50174-1 | 2008 | Information technology - Cabling installation - Part 1: Installation Specification and quality assurance - Requirements for installers of information technology cabling |
|  | MKS IEC 529 | 1995 | Degrees of protection provided by enclosures (IP code) |

Standards

All cables should be in accordance with latest version of:

- IEC 60227 –Polyvinylchloride insulated cables of rated voltages up to and including 450/700V

- IEC 60502 –Power cables with extruded insulation and their accessories for rated voltages from 1kV (Um = 1,2kV) up to 30kV (Um = 36kV)

- IEC 60245 –Rubber insulated cables – Rated voltages up to and including 450/700V

- IEC 60189 –Low-frequency cables and wires with PVC insulation and PVC sheath

- IEC 60702 –Mineral Insulated cables and their terminations with a rated voltage not exceeding 750V

- IEC 60228 –Conductors of insulated cables

- IEC 60331 –Tests for electric cables under fire conditions – Circuit integrity

- IEC 60332 –Tests on electric and optical fiber cables under fire condition

- IEC 60754 –Test on gases evolved during combustion of materials from cables

- IEC 61034-2– Measurement of smoke density of cables burning under defined conditions - Part 2: Test procedure and requirements

Selection

Permanent permutable current on all cables and conduits shall be in accordance with latest version of IEC 60364 –Electrical installations for buildings

All cables and conduits shall satisfy maximum voltage drop of 3% for lighting current circuits and 5% for other consummates where power supply is provided by public electricity and 5% for lighting circuits and 8% for other consumers.

Plastic pipes, boxes and other connecting elements

All plastic pipes, boxes and connecting elements shall be in accordance with latest version of EN 61386 for Conduit System for Cable Management.

Pipe diameter shall be minimum 16mm. Pipes should be guided on clamps with a distance of 50-60cm. Connecting points between pipes shall be made with fabricated connection part. Fabricated connection part should be also made for all curves of 90oC.

Mechanical protection of cables – pipes/tubes

Pipes and/or tubes shall be used for mechanical protection of cables. Pipes and tubes should be installed in accordance with vendor recommendation. Special attention shall be putted on entrance and exit of cable in order to prevent damage of insulation of cable. For LV installations, metal tubes and pipes shall be grounded. Tubes and pipes for outside installation should be protected from environmental impacts (galvanization,  plasticized).

Energetic 1 kV power cables

Delivery, mounting and connecting of power supply, cables and cables for distribution boards. Cables are laid in trench with insulation suitable for installation in a ditch.

The scope of works shall include supply, wiring through pipes, laying into previously excavated trench montage, connection of TT and IT cables. Including all required installation material, testing and commissioning, fully in accordance with requirements prescribed by the competent local “telecom” company

E.1.8  ELECTRICAL FINISHING WORKS

- patching all damages due to installation assembly works,

- remedy of eventual technical and/or aesthetics defects of the subject building installation, cleaning and taking debris out of the building,

- 60 days test operation.

E 1.9 CONTROL, TESTING AND MEASUREMENT

Upon completed inspection of the completed works, perform all tests as prescribed under prevailing regulations, such as:

- measuring insulation resistance of cables, electrical equipment and each piece of equipment separately and complete installation made,

- measuring transient grounding resistance,

- testing of complete installation made functioning, as well as functioning of each piece of equipment and/or installation separately, etc.,

- testing protection from voltage contact in the installation,

- measuring voltage drop in case user connection.

- Test contact between conductors,

- Test conductor discontinuance,

- Measuring of loop receiver resistance test

Measurements and issuance of a lighting certificate

The scope of work includes necessary photometric measurements - average brightness and issuance of a certificate by a licensed company.

Measurement and issuing of certificates for cables

The scope of work includes necessary measurements of the insulation resistance of 1kV cables, short-circuit testing - contact voltage, short-circuit testing - contact voltage, test contact between conductors, test break, measurement of resistance, test receiver loop and issuance of certificates from a licensed , accredited company.

Measurement and issuance of earthing certificates

The scope of work includes necessary grounding resistance measurements of all street lighting poles and other metal parts that may come under voltage and issuance of a certificate by a licensed, accredited company.

# E 1.10 FINAL PHASE -BUILT STAGE

## As buit drawings

Based on executed survey of the executed external electric installations, as built technical documentation, As built design shall be prepared by the Contractor and delivered to the Supervisor. Contractor is also obliged to draw up guidelines for the operation and maintenance of installed equipment.

E 2 ELECTRICAL INSTALLATIONS IN BUILDINGS

Whenever local regulations, local standards (MKS), or any common practice of trade, are subject to any interpretation, clarification, ambiguity, or dispute, a ruling by the Supervisor shall prevail, always provided that such ruling shall be fully in compliance with, and shall be based on the subject local regulations, local standards (MKS), as well as in accordance with common practice of trade.

All works must be carried out precisely and professionally. Prior to application, the Supervisor must examine all material and all his comments referring to material and quality of work shall be obligatory for the Contractor. The agreed prices include all fully completed works, the final product, and ready for use.

TECHNICAL CONDITIONS, STANDARDS AND REGULATIONS

1. These technical conditions form part of electrical installations and are considered as binding for the Investor.

2. Electrical installations will be made according to the MKS norms, which refer to this type of work, plan, calculations and these technical terms.

3. The conductor for single-phase and three-phase voltage must be placed in the hose. All conductors belonging to an same electrical circuit can be placed in the same hose.

4. The metal hoses of the  hood  must not be used as neutral conductors or as earth conductors.

5. The interconnection between the conductors will be performed with connectors. Soldering of conductors in electrical installations is not allowed.

6. The extension of the conductors can only be assembled with connectors in the distribution boards.

7. Avoid placing parallel electric pipes with the chimney, and if this is not possible, the lines should be placed at a distance of 20 cm from the chimney.

8. In case of crossing the electrical conductors near the chimney, it is necessary to place the insulation.

9. Thermal insulation is placed between electrical tubes with high voltage and pipes, in case of parallel installation of insulated high voltage electrical cables with gas, steam, thermal and water pipes.

10. Cross-over and parallel areas for telephone wires and high-voltage current conductors should be at an angle of 90 °. The distance between the cables should be less than 10 cm, and in case it is not possible, an insulating sweeper with a thickness of 3 mm shall be installed.

11. In case of parallel installation of horizontal high voltage installation, telephone installation and low voltage electrical installation, in this case, the high voltage installation cables shall be placed 30 cm under the ceiling. Fire protection cables shall be placed 10 cm below the insulating fire detection cables. In any case, the telephone cables must be at a distance of 20 cm from the high voltage cables. The distribution boards of these cables should be placed opposite each other at an angle of 45º. Low-current conductors should be placed in separate hoses with separate junction boxes in order to be completely separated from the high voltage conductors.

12. In the case where the installation hoses pass through a partition wall between wet and dry rooms, the intestines should be positioned in such a way that they do not collect water in their openings. The hoses should be made of waterproof materials and placed in a way to provide a drop to the water. The same is true when the hoses set in place pass through the walls of the building, providing a drop to the outside.

13. In the case where the installation hoses pass through a wall partition between wet and dry rooms, the wet room ducts must be protected in dry rooms with tools designed for wet rooms.

14. When pipes similar to cables without protection (GOT or PGO) pass through a wall, they must be protected by metal pipes. It is recommended that the ends of the metal pipes do not come out of the wall, but end up in the wall and the openings on the wall to be rounded and filled with plaster.

15. Fixing the cable on the pipe must be performed at a maximum distance of 30 cm.  Cables up to 1.5 mm2 should be at a maximum distance of 40 cm. Cables with a cross-section above 1.5 mm2 to 4 mm2 should be fixed to a maximum distance of 30 cm. Cables with a cross-section above 4 mm2 to 10 mm2 should be fixed at a distance of more than 50 cm.

16. All cable hoses should be placed in a straight line other than the vertical ones.

A cut-in setting can only exist in exceptional cases.

17. The hoses should be placed in the walls, before the plastering, if the walls are completely dry.

18. If the hoses are placed in permanent dry rooms, then gypsum for pre-hardening of the gut will be used.

19. If the hoses are placed in rooms that are not permanently wet, in that case, gypsum will not be used, but rather a cement, plaster and hooks for pre-hardening.

20. The conductors must be placed in the hoses in a way to ensure easy removal and re-installation without difficulty.

21. The installation of the connection box is carried out at a distance not exceeding 6m. This box must be placed in a way to provide easy removal and re-installation without any difficulty. There must be no more than 2 knots between two boxes.

22. It is permissible to place conductors of various electrical circuits through the same box.

23. The switches must be connected to phase conductors.

24. The switches in the bathrooms and toilets must be placed outside of them and can be simple, if the room in which it is dry.

25. The switches are placed on the wall at a height of 1.5 m from the floor.

26. In the offices, the sockets are placed at a height of 0.5m from the floor

27. All sockets should be grounded.

28. The distribution boards shall be positioned so that the upper end should not be higher than 1.8 m

29. The cutting of concrete must not be done without prior consultation by the supervisory authority.

30. The neutral tube must not be protected by a switch nor be connected to a switch. The resistance of the neutral tube to the outermost places in the building and the distribution board must not exceed 2Ω.

31. After the completion of electrical installations, the resistance of the neutral tube (cable) with the switches removed, must be measured in order to control the corresponding connection and function at the same time.

32. When using a neutral conductor, the contractor as a precautionary measure should pay attention when connecting the neutral conductor to any place.

33. The color of the neutral tube (cable) must be the same with the entire installation, which is blue and when placed or divided it must be wrapped around the screw with a hook or ring and then ffixed well.

34. Take special care when connecting the neutral tube (cable) with the protective contact in the socket

35. The connection of neutral pipes (cables) through protective contacts is prohibited.

36. In addition to controlling the neutral conductor, it is necessary to perform the function control of all connections with the Ohm meter by the supervisory authority.

37. The contractor should be a professional company and be authorized to perform this type of installation.

38. The Contractor shall provide all the necessary certificates and attestations as well as measurements by the notified body after completing the work.

39. The contractor is obliged to study the project before starting work. In case there are some ambiguities, he should ask for an explanation from the designer.

40. Electrical installations from the distribution board to the consumer can be made when the exact connection point is known.

41. No changes are allowed in the project without prior approval given by the designer and the supervisory authority. If there is a need for greater change, it will be done only after a permit has been given by the revision commission from which the project is approved.

42. In the performance of electrical installations, the contractor shall follow the MKS standards relating to this type of work, plan, calculations and technical conditions.

43. The installations may be put into operation immediately upon receipt of a confirmation from the commission that it has been carried out in accordance with the project and the MKS norms for such type of building.

Standards and regulations

1. Latest version of the building law 130/09

2. Applicable regulations for electrical installations

3. IEC 60364 - Electrical installations in buildings.

4. IEC 60269-1/2 LV fuses

5. IEC 61024-1, MKS N.B2. 803, 804, 810 - Protection of objects from atmospheric discharges.

6. 3. EN 12464-1 - Interior lighting

7. 4. DIN VDE 5035 - Interior lighting

8. 5. EN 1838 - Safe lighting

9. 6. DIN VDE 67528 - outdoor parking lot lighting

10. 7. EN 13201 - Street lighting

11. 8. EN 60598 / VDE 0711 - Degree of protection of electrical equipment from

12. dust, moisture and voltage indirect contact

13. 9. DIN VDE 0250 - mounting conductors 0.5k

14. 10. DIN VDE 0276 - Power cables 0.6 / 1kV

15. 11. DIN VDE 0815 and 0816 - Installation of telecommunication cables

16. 12. ISO / IEC 11801 - LAN cables (internal information networks)

17. 13. DIN VDE 0882 - Halogen cables.

18. 14. DIN VDE 0888 - Fibber optic cables.

19. 15. ISO 6790 - Graphic symbols for elements of PP installations in buildings.

20. 16. BC. EN54: parts 2; 3; 4; 5; 7; 11; 12 - PP protection in buildings.

21. IEC 60947-2 LV circuit breakers and control mechanisms

22. IEC 61439-1/2 LV circuit breakers and control mechanisms

23. Network rules of EVN

24. International standards

25. International Electrotechnical Commission Publications (IEC)

26. International Organization for Standardization Publications (ISO)

27. European Norms prepared by the European Committee for Electrotechnical Standardization or European Committee for Electrotechnical Commission Publications (EN)

28. The requirements of the fire fighting team

All installations and electrical equipment should be certified for quality and subject to the approval and control of the supervisor. The Contractor is obliged to provide the necessary measures for the supervisor's access to the current works and installations, and also the Contractor should provide the supervisor with a sample and / or the technical documentation if the supervisor considers it necessary.

Electric Power Cable Installation Lying

Cable installation lying is not recommended if outside temperature is lower than - 5 C, or, cables shall be previously heated and laid as soon as possible.

Prior to commencement cable laying, the Contractor shall be liable to verify if drum is not secured (cable ends are not closed in factory) or cable is cut for voltage test; to close cable ends accordingly, immediately upon completion of tests; to inspect entire trench and check if it is ready for cable laying. During cable acceptance on drum, it is necessary to remove attest on factory testing from drum and check the data and compare them with drum plate. If there is no attest, voltage test shall be conducted on cable.

Conductors should be chosen in such a way that they meet the optimal engineering and economic conditions and be in accordance with the existing technical norms and standards for the performance of electrical installations in buildings. Laying of the cables is done manually. Permissible bending semi-diameters for 1 kV cables with PVC insulation are 12d (outer diameter of the cable. The ends of the cables should be marked with tags containing basic data about the cable and marking of the conductors. It is recommended directly before laying them.

LV equipment (230/400V)

Complete equipment shall provide continuous work in health facilities, with respect to the following conditions:

  - 230/400V, 50Hz, TN-S

  - Rated insulation voltage of 400V between two phases and 230V between phase and ground

  - Voltage level deviation is given in specification and/or drawings

  - Complete equipment should be designed to work shortly under industrial environment  with rated voltage of 6kV (1.2/50s)

  - Complete material and equipment should be new, unpacked and protected from mechanical damages and weather conditions. All damages of the material during transportation or on-site is at responsibility and cost of Contractor.

  - Contractor should submit technical documentation for complete material and equipment. Documentation should consist of all details needed for tender evaluation, including Manufacturer Authorization Form.

  - User manual and instruction for maintenance. After completion of work, Contractor should provide User manual and instruction for maintenance.

Exclusion applies, where this is different with specification or drawings.

Labeling

Labeling shall be on Macedonian language and in accordance with drawings. Labels should be made of white plastic with black or red signs.

Equipment testing

Testing of electrical equipment shall be done in accordance with appropriate standards and recommended procedures by vendor.

Additionally, wider scope of testing with functional testing of operational electrical system should be performed.

Functional test of fixed electrical installation should be performed in order to confirm that electrical installation is ready to perform expected functions and operation.

All current circuits shall be confirmed by using operation of their break in order to ensure that current circuit is installed in accordance with design. Test should incorporate following activities:

      - Turn on and off of lighting circuits in order to prove that lighting circuit correspond with switch, protective device and sign

      - Turn off of main current circuits in order to prove that each circuit correspond with protective device and that protective device operate in accordance with designed functionality

      - Turning off of main switch/contractor in order to prove that proper current circuit is controlled by main switch/contactor

      - Turning off of all current circuits on all blocks to prove that insulation work properly

      - Turning off of all selector switches to prove that chosen sequence is in accordance with designed

      - To prove that protection devices respond accordingly with designed criteria

      - Other tests as per vendor recommendations and requirements of the Investor

Measurements and attest

After completion of electrical installations, following measurements shall be done by independent authorized company:

  - Resistance of the grounding probes

  - Insulation resistance of all circuits

  - Time off

  - Other measurements required by authorized bodies.

## E 2.1 SITE PREPARATORY WORKS

DISMANTLING OF EXISTING EQUIPMENT AND INSTALLATIONS

Dismantling, transportation to location, and disposal of electrical equipment at a dump site for electrical waste or a location determined by the investor at a distance of up to 10 km, of electric cables, installed  complete with brackets, clamps, pipes, hoses and plastic channels. The position includes the total dismantling of the entire cable installation ,  lightinf fixtures , anti panik light,switches, socket, distribution board and other small equipment

Before submitting the offer, the contractor is obliged to inspect the facility and to count and quantify in detail the equipment, the necessary tools and to estimate all costs for dismantling, transportation and disposal. The position includes a comlete lump sum value for all lights in the building.

## E 2.2 SUPPLY SYSTEM- DISTRIBUTION BOARD

| Standard number | Year | Title |
| --- | --- | --- |
| IEC 529 | 1995 | Degrees of protection provided by enclosures (IP code) |
| MKS N.A9.002 | 1982 | Identification of apparatus terminals – General rules for terminal marking using an alphanumeric notation |
| MKS N.A9.005 | 1985 | Code of designations of colours |

The Contractor shall not be under the obligation to produce symmetrical distribution within the cabinet, the Contractor shall be free to choose equipment location which shall serve the best to purpose. The exact cabinets dimensions shall be defined when the entire equipment shall be chosen. Upon testing and commissioning, the Contractor shall be under the obligation to deliver as build drawings on plasticized sheets for placing on beck side of cabinet’s doors, as well as, a CD electronic copy.Rated short-circuit breaking current and rated permanent current.

All LV blocks should be in accordance with expected short-circuit breaking current at that point. They also should be planned to provide uninterruptable operation under permanent full load.

Ingress protection of cabinets

Cabinets for LV switchgears and their equipment should be completely closed.

For inside installation, cabinets for rated load over 800 А should provide minimum IP 30 level of protection. For inside installation, cabinets for rated load below 800 А should provide minimum IP 40 level of protection. For outside installation, cabinets should provide minimum IP 54 level of protection. Class of protection could be with higher class, if this is required with technical description and drawings.

Class of protection of cabinets should be in accordance with IEC 60529.

Mechanical protection should be in accordance with IEC 62262.

Fire resistance of cabinets

All cabinets should be flame retardant for 750˚C/5s, in accordance with IEC 60695.

If it is possible, all elements, equipment and cabinets shall be from the same vendor. If one vendor could not provide all required elements, it is recommended to involve minimum number of vendors.

Equipment in switchboards

The piece protective equipment in switchboards should have the following characteristics

- Compact thermo-magnetic switch up to 125 A, 400V with breaking power 36kA according to IEC 60947-2 and EN 60947-2, Uc 690V, Ics=19kA, In= 20 – 125 A

- Compact thermo-magnetic switch up to 160 A, 400V with breaking power 36kA according to IEC 60947-2 and EN 60947-2, Uc 690V, Ics=36kA, In=160A

- Compact thermo-magnetic switch up to 63 A, 400V with breaking power 25kA according to IEC 60947-2 and EN 60947-2, Uc 690V, Ics=36kA, In=20 – 63A

- Differential protection switch with nominal current of 16 – 63 A, switching power 10 kA and differential protection current of 0.5; 03; 0.03 A (standard IEC61008-1). The switch should have the possibility of sealing and a visible flag to indicate the position of the switch on/off, as well as the possibility of installing the same copper busbar as the automatic fuses.

- Differential protection assembly from 16 – 63 A with "B" disconnection characteristic type:

1p +N; 3p + N

- Automatic fuses from 10 – 63 A with breaking power 6kA according to IEC 60898. The fuse must have separate connections for placing a copper busbar on the upper and lower sides as well as a flag for visible indication of the state of the fuse (on/off).

- Automatic fuses with "B" disconnection characteristic type: 1p C; 2p - module; 1p+N - 1 module, 3p В 6kA, 1 module 3p+N В 6Ka, 10 – 63 A with breaking power 6kA according to IEC 60898. The fuse must have separate connections for placing a copper busbar on the upper and lower sides as well as a flag for visible indication of the state of the fuse on /off B.

- Automatic fuses with "C" disconnection characteristic type: 1p C; 2p - module; 1p+N - 1 module, 3p В 6kA, 1 module 3p+N В 6Ka, 10 – 63 A with breaking power 6kA according to IEC 60898. The fuse must have separate connections for placing a copper busbar on the upper and lower sides as well as a flag for visible indication of the state of the fuse on /off C.

- Manual modular switch "1-0" and "1-0-2" of 16-40 A, 1P - 220V /3P 380V, Ui = 1000V, Uimp=4kV, Icw=800A, , Icm=500A, with rated covers of peaking 320A and nominal production covers 400A, manufactured according to IEC 60947-3, degree of protection IP 20, with an operating temperature of -25 0 C - + 55 0 C

- Modular contactor of 10-20 A, 230V, 1P /2P, manufactured according to IEC 947-4-1, IEC 947-5-1, VDE 0660, EN 947-4-1, EN 947-5-1, with lifetime contact life 0.1, minimum switch voltage 24/100, with a short-term current of 72 -340

- Modular contactor of 25-63 A, 400V, 2P /4P, made according to IEC 60947-4-1, IEC 60947-5-1, VDE 0660, EN 947-4-1, EN 947-5-1, with lifetime contact life 0.15, minimum switch voltage 24/100, with a short-term current of 72-340

- Surge protection manufactured according to IEC/EN61643-11, category II/T/C, number of poles 3+1, 20-40kA, with protection level < 2.0 kV, activation time < 25 ns, residual current < 0.2mA

- Modular disconnector with cylindrical fuses 10x38 made according to IEC 60947-1, IEC 60947-3, UL 4248-1, UL4248-8, UL486E, with cylindrical cartridge class gG, up to Imax = 50A, with breaking capacity of 32 kA

- Modular disconnector with cylindrical fuses 22x58 made according to IEC 60947-1, IEC 60947-3, UL 4248-1, UL4248-8, UL486E, with cylindrical cartridge gG, up to Imax = 100A, with breaking capacity of 120 kA

- Compact disconnector for NV fuses - horizontal made according to IEC DIN EN 61439-1 - 10.10.4.2, 3P-9W, with blade cartridges type NV, class gG, up to Imax = 160 A, Un 400 V, with breaking power of 120 kA , short circuit time 5kA/1s, IP20, sizes according to DIN VDE 0636-2, operating temperature -25 0 C - +500 C, with nominal insulation voltage 1000АС.

- cartridge type NV0, class gG, with In = 125 A, Un 400 V, with operating current of 2 – 1600A, breaking power of 120 kA, dimensions according to VDE43620 partition 1-4, certified according to DIN VDE 0636-201 (1998) -06), manufactured according to IEC 60268-1:2005/EN60269-1:1998+A1:2005

- Astronomical time relay with operating voltage 230 V, with 2 outputs, with nominal current 2x 16A/250 V, 4 (without connection to the electrical network), 48 h (without batteries and without connection to the electrical network), class A, with working temperature -100 C - +40 0C, degree of protection IP20 (EN 60529), with battery CR2037-3V-220mAh, memory covers 40, with screen back-lit liquid crystal

- Pooch baton switch  Currant / voltage rating  200m a for 250 V, install contact resistance 50 mO max, installation resistance 2GO min. at 500 VAC, dielectric strength 1500 VAC for metal material, electric life et full load 500 000 cycles, operating temperature – 30 – 850, operation force 2N-5N, contact bounce 10 ms, mechanical life 1 000 000 cycles, torque 1.5 Nm for metal material, soldering 3500 for max. 5 seconds, case – Dailey phthalate  ( DAP) ( UL-94V-0), cap -Polyamide 6/6, douching- Polyamide 6/6, IP 67, Certificate RoSH 2011/65/eu&2015/83

E.2.4.1 Distribution Boards

Distribution board MDB-MB

The distribution board MDB/M should be metal for wall mounting. High versatility and flexibility, removable internal set (can be wired in the workshop or on the site). Easy vertical dividing of enclosure by using, special separating elements, covers and mounting plates are dedicated for devices (MCCB’s, MCB‘s, RCBO‘s disconnectors, etc.).  Short assembling time, demountable door frame in flush-mounted version.  Two door locks with keys in standard equipment. High quality membrane cable flanges . Elements are precisely made of high quality, 1mm thickness sheet steel powder-coated, painted with polyester paint - UV resistan.t Safety class (total insulation) I , protection degree IP44, degree of protection against mechanical impact IK10, rated current 250V, ambient temperature,-5°C ... +40°C. Standard IEC/EN 62208, IEC/EN 60529, IEC/EN 62262, directive RoHS

Distribution board MDB/A

The distribution board MDB/M should be metal for wall mounting. High versatility and flexibility, removable internal set (can be wired in the workshop or on the site). Easy vertical dividing of enclosure by using, special separating elements, covers and mounting plates are dedicated for devices (MCCB’s, MCB‘s, RCBO‘s disconnectors, etc.).  Short assembling time, demountable door frame in flush-mounted version.  Two door locks with keys in standard equipment. High quality membrane cable flanges . Elements are precisely made of high quality, 1mm thickness sheet steel powder-coated, painted with polyester paint - UV resistan.t Safety class (total insulation) I , protection degree IP44, degree of protection against mechanical impact IK10, rated current 250V, ambient temperature,-5°C ... +40°C. Standard IEC/EN 62208, IEC/EN 60529, IEC/EN 62262, directive RoHS

Distribution boar DBF1/M

Distribution board DBF1/M should be modular type,  with housing made of non-flammable plastic, halogen free for wall mounting,  metal door  with against mechanical impacts IK 8. Мetal DIN rail TH35,  PE/N terminals - mounting set with screws , marking stickers with symbols , covers for mounting holes , cover for empty modular spaces. Rated voltage  400 V, rated current 100A, protection class  II. Glow wire test 6500. Standard PE-EN 62208-2011

Distribution boar DBF1/A

Distribution board DBF1/A should be modular type,  with housing made of non-flammable plastic, halogen free for wall mounting,  metal door  with against mechanical impacts IK 8. Мetal DIN rail TH35,  PE/N terminals - mounting set with screws , marking stickers with symbols , covers for mounting holes , cover for empty modular spaces. Rated voltage  400 V, rated current 100A, protection class  II. Glow wire test 6500. Standard PE-EN 62208-2011

E 2.5 CABLES AND METAL METAL  PNK  CABLR  TRAY

Standards

All cables must comply with the latest editions of:

- IEC 60227 - Polyvinyl chloride insulated cables for rated voltage up to and equal to 450/700V

- IEC 60502 - cables with extruded insulation for rated voltages from 1kV to 30kV

- IEC 60245 - Rubber insulated cables for rated voltage up to and equal to 450/700V

- IEC 60189 - PVC-insulated and PVC-sheathed low-frequency cables

- IEC 60702 - cables with mineral insulation for nominal voltage up to 700V

- IEC 60228 - conductors for insulated cables

- IEC 60331 - fire resistance characteristics of electric cable

- IEC 60332 - testing of electrical and fiber optic cables under fire conditions

- IEC 60754 - emission of halogenated substances during fire

- EC 61034-2 low smoke density

Choice

The permanent permissible current of all cables and conductors shall comply with the latest editions of IEC 60364 - Electrical installations in buildings and IEC 60364-7-710 - Electrical installations in hospitals.

All cables and conductors should be sized to meet the requirement for a maximum permissible voltage drop of 3% for lighting circuits and 5% for other consumer circuits, when we have mains power, i.e. 5% for lighting circuits and 8% for circuits for other consumers, when we have power supply they are supplied from a substation.

In doing so, it is necessary to generally satisfy the following minimum sections:

- 1.5 for bells and control circuits

- 1.5 for lighting

- 2.5 for sockets

Plastic pipes, boxes and accompanying connecting elements

All plastic pipes, boxes and fittings shall comply with the latest editions of EN 61386 for pipe systems for cable distribution.

The diameter of the pipes must not be less than 16mm. Pipes should be guided on brackets at a distance of 50-60 cm. At the joint between two pipes, a factory-jointed part should be provided, and for all 90˚ bends, a factory-made part should be provided.

Mechanical protection of cables – pipes/hoses

Pipes/hoses should be used for mechanical protection of the cables when they are laid on top. Pipes or hoses should be secured properly and special attention should be paid to the entrance or exit of the cable from the pipe-hose so that it is not crushed or its insulation is not damaged. When laying high-current installation, metal pipes and hoses must be grounded.

Pipes or hoses, if they are laid in an external environment, should be protected from atmospheric influences (to be galvanized, plasticized, etc.).

If the pipes and hoses are laid in the ground, they should be plastic, unless otherwise specified.

Cables for 0.4kV distribution - connecting distribution board to distribution board

E.2.5.1Method of installation- type 1

Procurement, installation and connection of power supply, 1kV cables for connecting the main board with the local board. The cables are led partly in a plasterboard wall , in the suspended ceiling, and partly in the wall under the plaster in previously made slots in the wall. The ends of the cables should be made with appropriate cable terminations. The cables are copper and halogen free.

The price of the cable should also include: making slots in wall with appropriate dimensions, making holes in a concrete slab, laying the cable and fixing it.

Cables for 0.4kV distribution – connecting a distribution board  with the end consumer

E.2.5.2 Method of installation- type 2

Procurement, installation and connection of power cables, 1kV for connecting the distribution board with the final consumer. The cables are led partly on metal perforated PNK cable tray , partly in PVC ribbed hoses in a plasterboard wall and partly in a PVC ribbed hoses in concrete floor. The ends of the cables should be made with appropriate cable terminations. The cables are copper and halogen free.

The price of the cable should also include: making holes in the existing wall, laying the cable, fixing, making holes in the plasterboard wall for junction boxes 100x100, 150x100, F 78 mm, procurement of PVC junction boxes 100x100 , 150x100, F 78 mm, connecting the cables in the junction boxes in accordance with the project, placing the junction boxes and fixing.

E.2.5.3 Method of installation- type 3

Procurement, installation and connection of power supply, 1kV cables for connecting the panel with the final consumer. The cables are led partly on metal perforated PNK cable tray , partly in the wall under plaster and partly in a PVC hose in concrete floor. The ends of the cables should be made with appropriate cable terminations. The cables are copper and halogen free.

The price of the cable should also include: making slots with appropriate dimensions in a wall, making holes in a wall/concrete slab, laying the cable, fixing, making openings in a wall for junction boxes 100x100, 150x100 , Ф 78 mm, supply of PVC junction boxes 100x 100, 150x100, Ф 78 mm, connection of the cables in the junction boxes in accordance with the project, placement of the junction boxes and plastering

E.2.5.4 Method of installation- type 4

Procurement, installation and connection of power supply, 1kV cables for connecting the distribution board with end consumer.  The cables are led partly on metal perforated PNK cable tray an partly in PVC ribbed hoses in a plasterboard wall and  partly in a trench in the ground in metal plasticized SAPA hose. The ends of the cables should be made with appropriate cable terminations. The cables are copper, halogen free

Measurement and payment

Payment for works for complete works including cable terminations delivered to the ends of the cables, will be per m¹ of cable.

The price of the cable should also include: installation of PVC brackets.

E.2.5.5Method of installation- type 5

Procurement, installation and connection of power supply, 1kV cables for connecting the distribution board with end consumer.  The cables are led partly on metal perforated PNK cable tray,  partly in PVC ribbed hoses on PVC brackets on the ceiling and in PVC ribbed hoses on PVC brackets on the metal construction The ends of the cables should be made with appropriate cable terminations. The cables are copper, halogen free

Measurement and payment

Payment for works for complete works including cable terminations delivered to the ends of the cables, will be per m¹ of cable.

The price of the cable should also include: installation of PVC brackets, supply and installation of PVC wall boxes with protection degree IP 44 with dimensions 100x100, 150x100. and connecting the cables in the junction boxes in accordance with the project.

E 2.5.6  Perforated  galvanized PNK  cable tray

Supply and installation on ceiling (above suspended ceiling) horizontal perforated cable tray PNK complete with U-profile, clamps, console, junction tray and all elements and material needed. The position includes horizontal and vertical curves and everything needed to install a cable tary. The contractor is obliged to prepare a workshop drawing for the installation of the PNK cable tray with the cables in it before approval for the performance with detailed quantities of pieces.

Cable tray systems and support systems shall be manufactured in accordance with EN 61537, EN 50174, EN ISO 12944, BS EN 50174, EN 61914, BS EN ISO 14713 and BS EN ISO 1461.

The maximum deflection of cable ladder and cable tray supplied shall not be more than 20 mm with a load of 50 kg/m on a 3-meter support span. If cable ladder covers are used, they shall be of peak type with 30-degree slope.

Special accessories from the manufacturer of the cable ladder or tray shall be furnished as required to protect, support, and install a cable ladder/tray system.

E 2.6 PVC HOSE

PVC (halogen free) ribbed hose

All PVC hoses shall comply with the latest editions of:

- DIN 49018 – profile

- DIN 57100/VDE0100 – scope of application

- EN61386 – production

- DIN/EN61386-1 – 10.2 – pressure testing

- DIN/EN61386-1 10.3- cold bending test

- DIN/EN61386-1 12.2- resistance to temperature

- DIN/EN61386-1 10.4- fire resistant characteristics of the hose

- DIN/EN 61386-1 12.1- testing under fire conditions

- IEC 60754 - emission of halogenated substances during fire

- EC 61034-2 low smoke density

PVC (halogen free) ribbed hose F 13/16mm

Procurement and installation of PVC ribbed hose Ф 13/16.mm  accordance with the EN 50085-2-1 standard.

PVC (halogen free) Ribbed Hose for In Concrete Ф 16/20mm

Procurement and installation of PVC ribbed hose f 16/20, in accordance with the standard EN 50085-2-1.

PVC (halogen free) Ribbed Hose for In Concrete Ф20/26mm

Procurement and installation of PVC ribbed hose f 20/26, in accordance with the standard EN 50085-2-1.

Metal plasticized SAPA hose

Flexible metallic tubes usually in heavy-duty conditions. In comparison with rigid tubes, they have less thickness of wall and therefore shall have superior anti-corrosive. The ideal materials to be used in the manufacture of flexible metallic tubes must meet the following requirements: -working ability by plastic deformation, -good strength properties, -optimum thermal stability, -anti-corrosive properties. Material galvanized steel with plastic sheathing is made in black PVC (white and grey on request).

Metal plasticized SAPA hose ф 18

Procurement and installation of  plasticized metal hose Ф18mm

Metal plasticized SAPA hose ф 32

Procurement and installation of plasticized metal hose Ф32mm

E 2.7 INSTALLATION MATERIALS

Standards

Electrical accessories should be in accordance with latest version of IEC 60670 –Boxes and enclosures for electrical accessories for household and similar fixed electrical installations

Switches

Switches for lighting should be modular type, single pole and they should have characteristics as it is specified with the bill of quantity and the drawings. Switches for lighting should be in accordance with the standard IEC 60669.

Switches in the mechanical and electrical room should be surface mounted. Switches in the other rooms should be recessed, isolated, single pole, white color.

Switches should be installed at the height of 1.5m from the finished floor.

Modular switches 10A, white color, with a width of one module, with automatic connection, designed for installation in recessed or surface-mounted doses, floor boxes, mini pillars, conference blocks and parapet ducts, in compliance with IEC 60884, IP-20, IK-04 standards, unfireable 650°C/30s, with operating temperature from -5 to +50 °C, resistant to cleaning products(hexane,methulated,anios,surfanos,bactilysin).

Socket

Modular type sockets for rated power of 16А, for general usage, in accordance with IEC 60884.

Sockets intended for machine and electrical rooms should be on-wall mounted, IP-55, IK-07. All other should be in-wall mounted, completely insulated, white for public electricity, red for back-up power supply and green for IT protection system.

3-phase sockets for industrial consumer should be in accordance with IEC 60609.

Telephone sockets

Modular type sockets, in accordance with IEC 60603. If there are no other specifications, they should be RJ-45, on-wall mounted, with white color.

Computer sockets

Modular type sockets, in accordance with IEC 60603 and EN 50173. If there are no other specifications, they should be RJ-45, on-wall mounted, with white color.

TV sockets

Modular type sockets, in accordance with IEC 60169-2. If there are no other specifications, they should be RJ-45, on-wall mounted, with white color.

Blind covers for switches and sockets

Made by high-resistive materials, IK-10, fixed with high-quality fixtures.

Equipotential boxes

Rail for equipotential for each floor for connecting of all metal installation with green/yellow conductor.

Floor box

Motion detector; installation type: ceiling mounted; housing: UV stabilized polycarbonate; protection class: II; degree of protection: IP20; interrupting capacity of 230VAC, 50Hz; setting options: mechanically by adjusting controller, electronically by infrared; field of detection:360°; passive infrared technology, contact: make contact, with a range of L= 12 m.

Motion detector; installation type: ceiling mounted; housing: UV stabilized polycarbonate; protection class: II; degree of protection: IP20; interrupting capacity of 230VAC, 50Hz; setting options: mechanically by adjusting controller, electronically by infrared; field of detection:180°; passive infrared technology, contact: make contact, with a range of L= 12 m.

### E 2.7.1 SOCKET

Modular set with 1x2M safe sockets for wall mounting L+N+PE, 250V,50Hz 16A

The modular set includes - one modular socket 2M - L+N+PE 250V 16A, PVC box ф 60, carrier 2M and mask 2M

Making an opening in an brick wall should also be included in the price

Modular set with 2x2M safe sockets for wall mounting L+N+PE, 250V,50Hz 16A

The modular set includes - two 2M modular socket - L+N+PE 250V 16A, 4M PVC box, 4M carrier  and 4M mask. Making an opening in brick wall should also be included in the price

Single-phase

Single-phase socket in waterproof design for wall mounting L+N+Pe 250V 16A with degree of protection IP 44 complete with all auxiliary equipment and materials.

E 2.7.2 SWITCHES FOR LAMPS CONTROL

Modular set with 1x2M one-way switch for wall mounting, 250V, 50Hz 10A

The modular set includes – one -way modular circuit breaker 2M, 250V 10A, PVC box ф 60

carrier 2M and mask 2M. Making an opening in brick wall should also be included in the price

Modular set with 2x1M one- way wall-mounting switch 250V,50Hz 10A

The modular set includes - two 1M modular switch, 250V 16A, PVC box ф 60,

2M carrier and 2M mask. Making an opening in brick wall should also be included in the price

Modular set with 4x1 M one-way switch for wall mounting, 250V, 50Hz 10A

The modular set includes – 41M modular one-way switch  250V 110A,  6/7M PVC box

4M carrier and  4M mask. Making an opening in brick wall should also be included in the price

Modular set with 1x1M one-way switch for wall mounting , with a signal bulb 250V, 50Hz 16A

The modular set includes – one -way modular one-way switch with a signal bulb 1M, 250V 16A,

PVC box ф 60 carrier 1M and mask 1M. Making an opening in brick wall should also be included in the price

E 2.7.3 FLOOR BOX

Flor box -  DF1

Floor box for 12 module the with vertical  mounting version with.  Back box made by polypropylene alveolar for concrete floor Adjustable height from 75 mm to 110 mm. To be equipped with мodules wiring 10-module ores. Delivered with movable lid with 8 mm recess for carpet or vinyl , with openings for cable exit. Easy opening by large handle.

The following equipment should be installed in the floor box : Modular 2x2M socket white, 2x2M socket - red, 2x1M EU socket white  and 4x1M RJ 45 Cat6. Certified to IEC 60670-1 and IEC 60670-23 standard

Flor box -  DF2

Floor box for 10 module the with vertical  mounting version with.  Back box made by polypropylene alveolar for  concrete floor Adjustable height from 75 mm to 110 mm. To be equipped with мodules wiring 10-module ores. Delivered with movable lid with 8 mm recess for carpet or vinyl , with openings for cable exit. Easy opening by large handle.

The following equipment should be installed in the floor box : Modular 3x2M socket - red, 1x1M EU socket and 3x1M RJ 45 Cat6. Certified to IEC 60670-1 and IEC 60670-23 standard

Flor box -  DF3

Floor box for 12 module the with vertical  mounting version with.  Back box nade by polypropylene alveolar for for  concrete floor Adjustable height from 75 mm to 110 mm. To be equipped with мodules wiring 10-module ores. Delivered with movable lid with 8 mm recess for carpet or vinyl , with openings for cable exit. Easy opening by large handle.

The following equipment should be installed in the floor box : Modular 4x2M socket white, 2x1M EU socket white  and 4x1M RJ 45 Cat6. Certified to IEC 60670-1 and IEC 60670-23 standard.

## E 2.7.4  JUNCTION BOXES

## - Junction boxes for wall mounting - F78, 100x100, 100x150 with technical characteristics

## • Insulation class according to IEC 61140

## • Mechanical resistance IK 08

## • Type of material – halogen-free, in accordance with EN 60754-2

## • Thermal pressure with ball 850 C

## • 6500C heated wire test

## • Operating temperature -25 to +600 C

## - Junction boxes for wall mounting: 100x100, 100x150 with technical characteristics

• Insulation class according to IEC 61140

• Mechanical resistance IK 08

• Degree of protection IP 56

• Type of material – halogen-free, in accordance with EN 60754-2

• Thermo pressure with ball 850 C

• 6500C heated wire test

• Operating temperature -25 to +600 C

## E 2.8 ELECTRIC LIGHTING

Standards

Luminaries should be produced, installed and tested in accordance the following standards:

- IEC 60598 Luminaries

- IEC 60926 Auxiliaries for lamps – Starting devices – General and safety requirements

- IEC 60927 Auxiliaries for lamps – Starting devices-Requirements for performance

- IEC 62386 DALI standard (general parts, control gear specific parts, control device specific parts)

LED LIGHT TYPE A

Upgraded LED light with dimensions 595mmx595mm, 30.3 W, 4340 Lm, . Light fitting protection: IP20  Maximum ambient temperature: ta = 35°C, Maximum ambient temperature: ta = 0-25°C (version with emergency back-up source for 1 or 3 hours; M1h, M3h)  Maximum system efficacy: 143 lm/W  The watt and lumen values can vary by ± 7,5 %  Standard model - CRI > 80: 4000 K   MacAdam = 3 SDCM  Lifetime: 50,000 hours / L90B10 Diffuser: acryl (PMMA) sandblasted on both sides Body: steel sheet, white (RAL 9003) or silver (RAL 9006) color Cable gland: rubber (SBS), white Terminal block: screw less, five-pole  Securing of the cover: by the means of magnets  Electric equipment: LED modules, current driver or current driver DALI, Complete with a frame for mounting on a ceiling. CE, ENEC certificates.

LED LIGHT TYPE- B

LED light with. Diameter 300mm, height 85mm. Lamp power maximum 23W, 2810 Lm,  Light fitting protection: IP54, IK10  Maximum ambient temperature: ta = 35°C, Maximum ambient temperature: ta = 25°C (version with emergency back-up source for 1 hour; M1h)  Maximum system efficacy:120 lm/W The watt and lumen values can, in accordance with valid standards, vary by ± 7,5 %  Standard model - CRI > 80: 4000 K Lifetime: 50,000 hours / L80B20  Diffuser: translucent polycarbonate (PC), UV stable, impact-resistant Body: white polycarbonate (PC), UV stable, impact-resistant  Reflector: steel sheet, white colour (RAL 9003)  Rotary cap: polyamide + 10 % glass fiber  Sealing: polyurethane (PUR), foamed body groove  Cable glands: rubber, SBS Terminal block: screw less, five-pole (basic version)  Electric equipment: LED modules, current driver or current driver DALI.  CE, ENEC certificates. For mounting on a wall/ceiling

LED LIGHT TYPE- C

LED light with. Diameter 300mm, height 85mm. Lamp power maximum 16W, 2010 Lm,  Light fitting protection: IP54, IK10  Maximum ambient temperature: ta = 35°C, Maximum ambient temperature: ta = 25°C (version with emergency back-up source for 1 hour; M1h)  Maximum system efficacy:120 lm/W The watt and lumen values can, in accordance with valid standards, vary by ± 7,5 %  Standard model - CRI > 80: 4000 K Lifetime: 50,000 hours / L80B20  Diffuser: translucent polycarbonate (PC), UV stable, impact-resistant Body: white polycarbonate (PC), UV stable, impact-resistant  Reflector: steel sheet, white colour (RAL 9003)  Rotary cap: polyamide + 10 % glass fiber  Sealing: polyurethane (PUR), foamed body groove  Cable glands: rubber, SBS Terminal block: screw less, five-pole (basic version)  Electric equipment: LED modules, current driver or current driver DALI.  CE, ENEC certificates. For mounting on a wall/ceiling

LED LIGHT TYPE- D

Supply, transport and installation of an LED light. Diameter 95mm, height 59.5mm. Housing material aluminum die cast,  reflector material polycarbonate. Optic material polycarbonate .Optical cover/lens material polycarbonate. Lamp power maximum 8W with a tolerance of ±10%, output luminous flux minimum 650 lump with a tolerance of ±8%, 82lm/W color temperature of 4000K; color rendering index 85 (CRI 85). Operating hours 50,000 /min L90. Degree of protection minimum IP65, IK02.CE, ENEC certificates. For mounting in a suspended ceiling

LED LIGHT TYPE- E

LED surface waterproof lamp with a length of 1272mmx700mmx95mm. Lamp power maximum 37W, 5450 Lm Light fitting protection: IP66 Maximum ambient temperature: ta = 45°C, Maximum ambient temperature: ta = 0-25°C (version with emergency back-up source for 1 or 3 hours; M1h, M3h)  Maximum system efficacy: 151 lm/W  The watt and lumen values can vary by ± 7,5 % •Standard model - CRI > 80: 4000 K  Mac Adam = 3 SDCM  Lifetime: 50,000 hours / L90B10  Diffuser: translucent polycarbonate (PC), UV stable, impact-resistant  Body: grey polycarbonate (PC), UV stable, impact-resistant. • Reflector: steel sheet, white color (RAL 9003) Clips: polyamide + 15 % glass fiber or stainless steel + polyamide Sealing: polyurethane (PUR), foamed body groove  Cable glands: screwed PG 13.5, or rubber (SBS)  Distance part: polyamide + 10 % glass fiber  Terminal block: screw less, five-pole (basic version), or screwed • Installation: package contains stainless hooks and stainless brackets  Electric equipment: LED modules, current driver or current driver DALI CE, ENEC certificates. For mounting on a wall/ceiling

### ANTI-PANIC LED LAMP TYPE1

LED surface waterproof lamp with a length of 356mmx136mmx79mm. Lamp power maximum 2W, 150 Lm, 75Lm/W Recognizing distance: 25 m •Light fitting protection: IP42  Maximum ambient temperature: ta = 40°C • Diffuser: opal zed polycarbonate, UV stable • Body: white polycarbonate • Reflector: white polycarbonate • Mac Adam = 3 SDCM • Diffuser and body connected: by screws • Charging:M3h variants max. 24 h M3h at variant max. 12 h • Electric equipment: driver, emergency module 3h;  M3h variants including Ni-Cd HT battery (3,6V); For mounting on a wall/ceiling

### ANTI-PANIC LED LAMP TYPE2

Supply, transport and installation of LED surface waterproof lamp with a length of 356mmx136mmx79mm. Lamp power maximum 2W, 150 Lm, 75Lm/W Recognizing distance: 25 m •Light fitting protection: IP42  Maximum ambient temperature: ta = 40°C • Diffuser: opal zed polycarbonate, UV stable • Body: white polycarbonate • Reflector: white polycarbonate • Mac Adam = 3 SDCM • Diffuser and body connected: by screws • Charging:M3h variants max. 24 h M3h at variant max. 12 h • Electric equipment: driver, emergency module 3h;  M3h variants including Ni-Cd HT battery (3,6V). Complete with holder on the ceiling

### MOTION SENSOR

Motion detector; installation type: ceiling mounted; housing: UV stabilized polycarbonate; protection class: II; degree of protection: IP44; interrupting capacity of 230VAC, 50Hz; setting options: mechanically by adjusting controller, electronically by infrared; field of detection:360°; passive infrared technology, contact: make contact, with a range of L= 12 m. Lamp power maximum 2000W, time on off adjustable 10sec-40min with dusk control. For mounting on a ceiling.

Motion detector; installation type: ceiling mounted; housing: UV stabilized polycarbonate; protection class: II; degree of protection: IP20; interrupting capacity of 230VAC, 50Hz; setting options: mechanically by adjusting controller, electronically by infrared; field of detection:180°; passive infrared technology, contact: make contact, high occupancy of L= 12 m, Lamp power maximum 2000W ,time on off adjustable 10sec-40min with dusk control. For mounting on a wall.

# E 3. LOW CURRENT SIGNAL ELECTRICAL INSTALLATION AND EQUIPMENT

# E.3.1 FIRE ALARM SYSTEM AND ACCESSORIES SYSTEM

This system allows for quick detection with an automatic fire detector. The automatic fire detector detects the increased presence of burnt products. The information is sent to the addressable control panel which, according to pre-defined functions, manages a certain device: Turns on the sirens, turns off the ventilation, activates fire extinguishing through the modules, transmits information to the monitoring center and communication with the parallel panel.

The fire fighting system and the auxiliary system must contain the following equipment:

- Control panel addressable panel (FACP)

- Addressable optical smoke detector

- Addressable heat detector

- Addressable manual dialer

- Addressable siren

- Addressable input module

- Addressable input/output module

1. Self-contained addressable control panels are capable of operating in a stand-alone configuration. The panels should have LPCB, VDC and FM approval of EN54 and meet the regulatory requirements of the country.

2. Self-contained addressable control panels are capable of operating in a network of 32 panels and terminals or 16 panels if connected to the station management system. Panels should have LPCB, VDC and FM approval to EN54 and meet country regulatory requirements

3. Control panels must provide at least the following:

a. with housing, with two integrated detection circuits, or four extended circuits for connecting up to 252 devices.

In addition to the network panel, the extended circuit card allows doubling the number of circuits while saving the number of addresses.

c. One monitoring siren circuit.

d. Designated fire warning outputs for remote connection

ARC communication equipment. This circuit also provides reduced degraded mode operation in accordance with EN54 requirements for systems with more than 512 detectors.

is. Definite fire outputs with clean contacts.. Provides reduced degraded mode operation in accordance with EN54 requirements for systems with more than 512 detectors.

f. Definite fire warning fault outputs for connection of ARC remote communication equipment.

g. Determined defective outputs with clean contacts.

h. Assembled 24VDC warning systems to power EN54-4, with built-in battery up to 72hrs + 30 minutes full alarm.

i. construction of the panel will allow:

1) Sufficient cable entries for all connected detection circuits, siren circuits, network cables and main devices.

2) Attractively removable decorative front cover with metal back box providing minimum ingress protection of IP30.

3) surface or semi-flush mounting.

j. Manned / unmanned operation:

1) control panels should have dedicated fire warning communication at the exits and be able to work in two different ways:

Unmanned mode - Alarms from any manual pager or automatic detector will immediately send a signal to the fire department's communication equipment.

2) it should be possible to select the mode staffed with any of the following:

b) Automatically selected during working hours using the internal system clock with automatic switching to summer / winter time. It may be possible to extend the working time up to 4 hours (programmable) by pressing a special control. (Control for extension of working hours). This extension can then be canceled by pressing (cancel extension of working hours button). or

c) Manually selected the control button in the working rooms. or

d) Automatically selected when an intrusion is set. or

e) Automatic defenses with input from the access control system.

3) delays of communication equipment of the fire service can be canceled by pressing the alarm delay control on the control panel.

k. Presence of fault monitoring: the control panels should have a designated monitoring output to communicate with the fault communication equipment this should work in two different modes manned and unmanned mode.

1) Crew mode – The error activates the local alarm and the delay starts

t1 to monitor attendance. The operating personnel acknowledges a fault at the operating terminal before the expiration of T1, by silencing the local alarm equipment If the fault is not acknowledged, the global alarm is activated before the expiration of T1. At the same time as the T1 delay, the time for the service intervention starts in the 'monitoring intervention' section. If the fault is not eliminated before the expiration of ts, the maintenance personnel is called.

2) Unmanned mode –

Errors should be reported directly.

l. Requirements: Fire alarm control panels shall be capable of receiving and processing all of the following conditions from the device area:

1) Alarm

2) pre-alarm

3) device failure

4) damaged device

5) isolated device

m. Programmable functions:

Fire alarm control panels shall be capable of being configured to do all of the following:

1) manned / unmanned mode:

a) choice of time of day.

b) for choosing certain days.

c) to dial with remote input.

d) manual selection

e) Time programmable for attendance and time for examination

f) to dial for siren during the first timer, off, on or pulsating.

2) Behavior of the detector:

a) it should be possible to select the required parameter in the room for each panel detector, through the programming tool.

b) it should be possible to configure each individual device to operate within a manned / unmanned concept or not.

3) Cause and effect control:

a) Fire alarm control panels should have the ability to create complex cause and effect control, including AND, OR and NO function or their combinations.

b) In addition, the controls can be programmed in terms of panel functions and be linked to tim

Sirens:

It should be possible to select siren tones and volume from the control panel. Up to two different tones will be selectable for each siren and configured to work with different cause and effect scenarios.

Alarm indicators:

It should be possible to configure an individual LED extension to be triggered by any of several detectors.

n.Isolation – fire alarm control panels shall permit isolation of any individual device, zone, section or area. Any insulation must be capable of being regenerated after a predetermined period of time.

n.Renovation Mode - fire alarm control panels include a renovation mode that can be set during a temporary renovation. This mode sets all detectors in the selected area to a lower sensitivity "Renovation" set parameter.

n. Test modes - fire alarm control panels will allow the following tests to be performed:

1) test lamps - The control panel should include a control button, which will illuminate all panel indicators and highlight the completeness of the screen.

2) detector test - The control panel can be set in detector test mode. This increases the sensitivity of all detectors in that zone by setting the robustness parameter. During the test, the detector alarm indicator will be illuminated, but the sirens and controls will not activate. More basic sirens connected directly to the detector will operate briefly.

3) installation test - Control panel to be able to set zones in detector test mode. This increases the sensitivity of all detectors in that zone by setting the robustness parameter. On the indicator alarm test the detector will be illuminated and all programmed sirens and controls should operate as required.

4) Walk test - the operation panel can set groups in test mode

a walk. When the detector is activated, the alarm siren is activated for 10 seconds.

5) Circuit card detection (4 circuits)

6) circuit card extension

7) Circuit card detection for interactive addressable detector series (1 cycle)

8) Circuit card detection for interactive addressable detector series (1 template)

9) Circuit card detection for Synod LOOP addressable array detectors (4 circuits)

10) I / O card (programmable)

11) 2 x 4 siren cards.

12) Network cards.

13) RS232 interface card

14) RS485 interface card

o. the fire alarm panel should enable exchange of the faulty module and check that the firmware on the new card has the correct version for the main software application

b. The control panel should allow you to configure which categories should be displayed

q. Programmable time for inputs before they are considered active.

r. Alarm counter, which can be set with parameters for:

1) Alarm counters from one or more fire control panels

2) Test alarms will be considered as YES / NO

s. Modules with optical fiber cable network single mode 40 km, multi mode 4 km

ADDRESSABLE FIRE PANEL

Addressable fire panel  with 1 loop / 250 addressable PP devices, capacity of the current circuit 500 mA, 8 zones, 4 relay outputs, 2 outputs (controlled, programmable, relays), Power supply (18-26) V /1.5 A, event memory 1240 events, LCD display 4* 20 characters , multilingual, programming – DMT Tech sowtver, R5485 output interface. Made according to EN-45-2 and EN-45-4

ADDRESSABLE OPTICAL – SMOKE DETECTOR

Smoke detectors are intelligent devices with integrated algorithms for comparison with real sensor signals, ensuring fast and reliable detection. Detectors should meet and be approved by EN54-7. The detector should be designed to have a high level of tolerance to dust, dirt, temperature fluctuations and air currents. In addition, the detector should contain:

1. Selection of specific application set parameters.

2. Communication of 3 different danger levels for differentiated alarm activations

3. Ability to detect if the detector is in an inappropriate environment and give a special warning about it on the panel

4. Gradual penetration of dust and dirt, to ensure a consistent level of detection over time. When the detector reaches a tolerance point where it can no longer tolerate the possibility of detection by a special warning signal given to the control equipment.

5.Compound Insulator Short Circuit.

Separately controlled remote output indicator for activation, or other detectors.

Indicator with put response with 360 viewing angle.

The operating temperature ranges from -10 C to + 55 C

EMC compatibility 50V / m

ADDRESSABLE HEAT DETECTOR

Heat detectors should be intelligent devices with integrated algorithms for comparison with real sensor signals ensuring relevant detection. Detectors should meet and be approved by EN54-5. In addition, the detector should contain:

1. Application selection for a specific parameter set

2. Communication of 3 different danger levels for differentiated alarm activations.

3. Internal fault monitoring with special signal fault report to the control panel.

4. Integrated short circuit isolator.

5. Separate controlled remote output indicator for activation by this or other detectors.

6. integral indicator with 360 ° viewing angle.

7. Operating temperature range from -10 ° C to + 55 ° C

8. EMC compatibility at 50V / m

ADDRESSABLE MANUAL CALL POINT (AMCP)

Manual call point with shrinkable glass type suitable for flat or surface mounting and approved by EN54-11 and EN54-17. The manual call point should also contain a test button for quick testing of the device, without removing the glass. The manual dialer also consists of the following:

1. Integrated short circuit isolator.

2. Alarm indicator.

3. Space for adding an additional protective door.

A wireless communication device to facilitate testing; which allows reading the current state and diagnostics of wires.

Operating temperature: -25 ° C to + 70 ° C

EMC compatibility at least 50V / m

Full protection of at least IP44 protection

ADDRESSABLE SOUNDER - INTERNAL

Addressable alarm siren, which should be for power supply in a loop. They should meet the requirements to be approved by EN54-3. In addition they should:

- Have a built-in short-circuit isolator in the event of a short-circuit on the loop, the siren / signal must continue to sound.

- Have locking capability to prevent unauthorized removal.

- To have 11 programmable tones to choose from the panel.

- To have the ability to choose between warning and evacuation tones.

- Be fully synchronized with other sirens connected to the control panel.

- To have 3 settings for selecting the volume from the panel.

- To be able to provide a power of at least 99dBA at 1m.

- To be painted red with RAL 3000

- Operating temperature in the range from -25 ° C to + 70 ° C

- To have a minimum of EMC compatible at 50V/m

ADDRESSABLE SOUNDER WITH STROBE - OUTDOOR

Supply and installation of flasher alarm sirens shall be addressable units connected and powered directly on a loop. They should meet the requirements and be approved by EN54-3 and EN54-17. In addition they should:

Supply and installation of flasher alarm sirens shall be addressable units connected and powered directly on a loop. They should meet the requirements and be approved by EN54-3 and EN54-17. In addition they should:

- Operating temperature in the range from -25 ° C to + 65 ° C

- To be painted in orange transparent color

- Have a built-in short-circuit isolator in the event of a short-circuit on the loop, the siren / signal must continue to sound.

- Have locking capability to prevent unauthorized removal.

- To have 11 programmable tones to choose from the panel.

- To have the ability to choose between warning and evacuation tones.

- Be fully synchronized with other sirens connected to the control panel.

- To have 3 settings for selecting the volume from the panel.

- To be able to provide a power of at least 99dBA at 1m.

- To have a maximum output of at least 3.2cd

- To be painted in orange transparent color

- To have a working temperature range

- Minimum EMC compatibility of 50V/m

ADDRESSABLE INPUT / OUTPUT MODULE

- Input / output modules should comply with the requirements and be approved by EN54-17. Input / output modules should be connected directly to the loop and require no further power connections. Each input/output module should take one address, but has four separate programmable inputs and four separate programmable outputs. Input / output modules additionally include:

1. Short and open circuit inputs.

2. Inputs can be configured for normally open and normally closed operation.

3. Outputs Payment to be rated at 250VAC 4A resistive and 30Vdc 4A clean contacts.

4. The outputs have a choice of continuous or pulse operation. Pulse duration to be a choice between 1 and 20 seconds.

5. Composite short circuit insulator.

- 6. LED indication of normal, fault, test, and activation conditions.

7. Possibility of configuration for safe operation in case of failure.

8. Programmable filter activation delay from 0-240 seconds.

9. The modules should be mounted in IP54 housings with a clear cover to indicate the status of the device.

10. Where modules are to be placed outside or in other areas, where they are likely to be exposed to moisture or splashed with water they should be mounted in an IP66 enclosure with a clear cover to indicate the status of the device.

11. Modules should additionally be suitable for DIN rail mounting.

12. Operating temperature: -25 ° C to + 60 ° C

13. EMC compatibility: 50V / m

Type of cables and laying method

- Type - JE-H(st)H 2x2x0.8 mm, ( Halogen Free )

- Type JE-H(st)H 2x2x0.8 mm, FE 180 E30/E90 (Halogen Free)

The cables are routed in PVC hoses in the ceiling part, in the suspended ceiling, and in PVC piped in the wall under the plaster in PVC pipes in pre-made slots in the existing walls. The ends of the cables should be made with appropriate cable terminations. The cables are copper and halogen free as type:

The cables are led partly in PVC ribbed hoses in a plasterboard wall  or in the wall under plaster and partly  on a PVC/metal carrier for ceiling/wall. The cables are halogen free.

The price of the cable should also include: making slots in plaster with appropriate dimensions, making holes in an existing brick/concrete wall, laying the cable, fixing.

The price of the cable should also include PVC carrier for cable JE-H(st)H 2x2x0.8 mm,  and metal carrier for cable JE-H(st)H 2x2x0.8 mm, FE 180 E30/E90

FIRE SYSTEM MONITORING SOFTWARE, TECHNICAL DOCUMENTATION, DETECTION SYSTEM INTEGRATION, COMMISSIONING

Procurement and installation of appropriate to the selected equipment, software. The system should be suitable to be controlled by a remote computer using software that can be dialed with the connected panel to enable remote inquiry and operation. The software should be set up to appear as a direct copy of the control panel and be capable of displaying all information and controlling all features of the panel itself.

The entire system will be inspected and tested to ensure that it operates in accordance with this specification and country requirements. Especially that:

1. All manual call points and automatic fire detectors are functioning properly.

2. All devices carry an accurate identification label.

3. All manual call points and automatic fire detectors, when operating, result in correct text and zone marking on all indicating equipment.

4. The sound pressure level meets the requirements of the country.

5. The connection to the ARC (Fire Service) is working properly.

6. System causes and effects meet the requirements of this specification.

7. All manual call points and automatic fire detectors meet the requirements of the country.

8. All auxiliary functions such as lift-returns, boiler shut-off and mechanisms for etc.9. All fault indicators and their relevant circuits are verified by simulating appropriate fault conditions.

10. Read and record all insulation resistance, ground continuity and circuit impedance.

After the completion of the system, the contractor will submit the following documentation:

1. One set of drawings for record system and wiring details in printed and CAD format.

2. Two sets of system management, installation and maintenance manuals.

3. Complete registers of embedded devices, their programmed parameters, texts and tasks.

4. Documentation of all programmed causes and effects.

5. Documentation of the topology of the actual field of conducted wires.

6. A copy of the system programming in CD or floppy disk format.

7. System ledger.

Measurement, testing, training and certificates

1. The contractor is obliged to provide full system management training and accountability to at least two people nominated by the clients.

Upon completion the contractor will provide the following certificates in accordance with the country's regulation:

1. Design certificate.

2. Installation certificate.

3. Confirmation of commissioning.

4. Certificate of Acceptance

5. Examination of the entire firefighting installation and equipment by a licensed company and obtaining a certificate of correctness and functionality

Fire Fighting extinguishing devices

Reference

ЕН 3-7+А1:2008, ЕН 3-8:2007, ЕН 3-10:2010

CE and ISO 9001:2009 certificates

Fire Fighting apparatus S9 shall be used in the initial extuingishing of a indication of fire. It shall be under constant pressure and shall be refilled in for next use.The pressure shall be visible on the manometer on the valve.

Fire Fighting apparatuse CO2-5 kg shall be used for extinguishing initial fires of class B, C and for electrical equipment under a voltage of 1 000 V. The device shall be refilling, if necessary

E.3.2 VIDEO SURVEILLANCE SYSTEM - CCTV SYSTEM

The system must be based on IP cameras, connected through an independent IP network for video surveillance and monitoring

This system should be able to store 31 days of recorded material from these cameras, and 15 days with the highest resolution (1920x1080) and full intensity of frames, while the rest of the days with the highest resolution but with reduced intensity of frames – DOI frames of H. 624 compression, not less than 2fvs. All recordings in the event of an alarm must be stored in non-reduced format (full frame intensity) for as many days as will be agreed with the user.

NETWORK VIDEO RECORDER – NVR

Delivery and installation of a video recorder with the following features:

All-in-one video recorder, network video surveillance system overview and control, 42-channel recording capability with 8 pre-licensed channels. Processor Intel i3-8100 processor, Chipset Intel Q370, Memory installed 8 GB SO‑DIMM, Network ports 2 x RJ45 Gigabit Ethernet LAN, 4 trays: 3.5‑inch SATA.

NETWORK SWITCH – PoE

Supply and installation of  PoE switch.

10/100/1000BASE-T Gigabit Ethernet ports, 2 extra Gigabit TP ports and 2 1000BASE-X SFP interfaces with the inner power system. With a total of 185 watts of PoE budget

MEMORY HARD DISK – HDD

Supply and installation in a digital video recorder, setup and warranty support of a professional 4x4TB HDD, intended for work 24/7 Sill Tram TM

IP CAMERA TYPE 1

Delivery and installation of a video recorder with the following features:

Delivery and installation of an indoor dome camera for indoor installation with the following features:

5MP resolution, 1/2.9 inch CMOS, Color 0.5 lx, High Dynamic Range 120 dB WDR, Lens type 2.8 mm fixed, F1.6, Distance 15 m, H.265; H.264; M- JPEG, 20 fps, HDR, 3072 x 1728 (5.3 MP), 25 fps, HDR, 2720 x 1530 (4.1 MP), Noise reduction, Intelligent defog, Privacy Masking, ONVIF Profile S; ONVIF Profile G; ONVIF Profile T: GB/T 28181, TLS1.0/1.2, AES128, AES256, Water/dust protection IP42, POE IEEE 802.3af / 802.3 at Type 1, Class 3 12 VDC ±30%, The camera is intended for recording the internal hall

IP CAMERA TYPE 2

Delivery and installation of a camera for outdoor installation with the following features:

CMOS 1/2.9", resolution 3072 (O) x 1728 (V) 5.3Mpx, Color 0.379 lx, 120 dB WDR, compression H.265; H.264; M-JPEG, IR range up to 30m, recording with 20 fps, HDR, 3072 x 1728 (5.3 MP), 25 fps, HDR, 2720 x 1530 (4.1 MP), Backlight compensation, Noise reduction, Intelligent defog, Motorized Lens type 3.2 to 10 mm, Privacy Masking, Memory card slot micro SDHC / micro SDXC SD card slot, Audio line in , Audio line out, Alarm input, Alarm output, Ingress protection IP66, ONVIF Profile S; ONVIF Profile G; ONVIF Profile T: GB/T 28181, POE IEEE 802.3af / 802.3 at Type 1, Class 3 12 VDC ±30%.

PACH PANEL

Delivery and installation of a full patch panel with 24 x RJ45 ports for connecting the cameras to the NVR

CONECTORI RJ45 Cat 6a

Delivery and installation of RJ45 Cat6a connector for cable termination and camera connection

CCTV MONITOR

Supply and installation of LCD 24 "monitor, 1920x1080 Full-HD resolution with HDMI port CCTV LED monitor 42 "(107cm); 1920x1080 Full-HD resolution, 3000: 1 contrast, 2 ambient temperature, storage -20 to +60 ° C

POWER SUPPLY

Description

Supply and installation of mains power supply 220/12 V, 10A.

CABLE

Procurement and installation of cables:

- Type – LSHF U/FTP 4x2 x 0.51 mm Cat6a, ( Halogen Free )

The cables are led partly on metal perforated PNK cable tray , partly in PVC ribbed hoses in a plasterboard wall  or in the wall under plaster, included connectors on both sides of the link. The cables are halogen free.

The price of the cable should include connector RJ45 Cat 6, at both ends of the cable also include: making slots in plaster with appropriate dimensions, making holes  in an existing brick/concrete wall, laying the cable, fixing

Measurement, testing, training and certificates

1. The contractor is obliged to provide full system management training and accountability to at least two people nominated by the clients.

Upon completion the contractor will provide the following certificates in accordance with the country's regulation:

1. Design certificate.

2. Installation certificate.

3. Confirmation of commissioning.

4. Certificate of Acceptance

5. Examination of the entire network video installation and equipment, testing the link by a licensed company and obtaining a certificate of correctness and functionality

E .3.3. TELEPHONE AND COMPUTER INSTALLATION

RACK CABINET 19”, 42 U

Delivery and installation of a 42U, 19”,  free-standing rack cabinet, with the following features:

Dimension: 800 x 800 x 2050 (+/- 2mm)Material: Metal Front door: Glass and lock

Color: Black RAL9004 electrostatic paint. The cabinet should be equipped with :

1 .F.O. Patch Panel, 19", 1U, 24-ports, SC/PC, SM, full, psc1

2.  19" metal empty patch panel 1U, 24xGG-45/s connection point Cat.6a, with cable holders and

mark  psc . 5

3 .Patch cord, Fiber Optic, SC/PC - SC/PC, Single Mode, 50/125um, duplex, L=1,5m. pcs. 24

4. Delivery and mounting of a connector RJ-45, U/FTP,Cat6a, Keystone Jack pcs .152

6.19" patch cord organizer, PVC duct, 1U panel for managing cables (patch cords). pcs. 5

7. Power strip with 9 sockets and surge protection pcs. 1

8. Panel with 4 fans and a thermostat for installation in a cabinet pcs. 1

9. Metal shelf for installation in a wardrobe pcs. 2

TYPE 1 COMPUTER SOCKET Description

Modular set with 1x1M computer / phone socket  RJ 45 Cat 6a for wall mounting

The modular set includes - one RJ 45 Cat6a 1M modular headset, Ф 60 PVC box, 1M carrier and 1M mask, kit with connector RJ45 Cat6а

Modular set with 2x1M computer / phone socket  RJ 45 Cat 6a for wall mounting

The modular set includes - one RJ 45 Cat6a 2M modular headset, Ф 60 PVC box, 1M carrier and 1M mask, kit with connector RJ45 Cat 6а

CABLE

- Type – LSHF U/FTP 4x2 x 0.51 mm Cat6a, ( Halogen Free )

The cables are led partly on metal perforated PNK cable tray , partly in PVC ribbed hoses in a plasterboard wall  or in the wall under plaster and in PVC ribbed hoses in concrete floor. The cables are halogen free.

The price of the cable should also include: making slots in plaster with appropriate dimensions, making holes in an existing brick/concrete wall, laying the cable, fixing

Type – RU213/U,50Ohm

Coaxial Cable Solid Polyethylene Insulation, Bare Copper Braid Low Smoke Halogen Free (LSHF) Black Sheath. Construction Conductor Material : Bare Copper Conductor Size : 7/0.75 mm Dielectric : Solid Polyethylene (SPE) Diameter of Dielectric : 7.25 mm Screen Material : Bare Copper Wire Braid (≥97% Coverage) Outer Sheath Material : Low Smoke Halogen Free (LSHF) Outer Sheath Colour : Black Electrical Characteristics Impedance : 50 Ω ± 3 Capacitance : 100 pF /m ± 3 Velocity of Propagation : 66 % ± 3 Max. Conductor Resistance : ≤ 6.0 Ω /km Max. Screen Resistance : ≤ 4.4 Ω /km Voltage Rating : 30V

Physical Characteristics Overall Diameter : 10.3 mm (±0.10mm) Min. Bend Radius : 10 x OD Temperature Rating : -20°C to +70°C Weight : 166 kg/km

Standards Flame Retardant : BS EN 60332-1-2 RoHS3 Compliant : Yes CE Compliant : LVD (2014/35/EU), CPR (305/2011) CPR Classification : Eca (EN50575:2014+A1:2016)

The cables are led partly on metal perforated PNK cable tray , partly in PVC ribbed hoses in a plasterboard wall  or in the wall under plaster. The cables on the roof should be laid in metal  plasticized SAPA hose

Measurement, testing, training and certificates

1. The contractor is obliged to provide full system management training and accountability to at least two people nominated by the clients.

Upon completion the contractor will provide the following certificates in accordance with the country's regulation:

1. Design certificate.

2. Installation certificate.

3. Confirmation of commissioning.

4. Certificate of Acceptance

5. Examination of the entire network video installation and equipment, testing the link by a licensed company and obtaining a certificate of correctness and functionality

E 4. LIGHTNING ROD INSTALLATION AND GROUNDING

Standards

Earthing and lightning protection should be in accordance with the latest editions of the following standards:

1. IEC 60364 Electrical installations in buildings

2. IEC 62305 Protection against atmospheric discharges

3. IEC 61643 Overvoltage protection

4. MKS N.B4 801 Protection of objects from atmospheric discharges - General conditions

5. MKS N.B4 803 Protection of objects from atmospheric discharges – Average annual number of days with thunderstorms

6. MKS N.B4 804 Protection of objects from atmospheric discharges - Tolerated frequency of atmospheric discharges

E 4.1 LIGHTNING PROTECTION INSTALLATION

-Procurement and installation of metal hot-dip galvanized strip FeZn 25x 4 mm with zinc coating Z 500, EN 62561-2. The strip is led on installed roof supports

-Procurement and installation roof tape carrier - straight/twisted

The payment of works shall be made per piece for the completely executed work

- Procurement and installation junction piece, for joining strips with strip

-Making a joint of tape with metal pole by welding. The joint should be protected with an application of oily paint.

-Procurement and installation of circular frame for metal pipe Ф 5/4"

E 4.2 GROUNDING

| ICS Number | Standard number | Year | Title |
| --- | --- | --- | --- |
| E 1 | MKS C.K5.030 | 1972 | Galvanized metal earthling strips – Technical requirements for manufacturing and delivery |

-Procurement and installation of metal hot-dip galvanized strip FeZn 30x 4 mm with zinc coating Z 500, EN 62561-2 . The strip is led in a dug trench in the ground

- Procurement and installation junction piece, for joining strips with strip

-Making a joint of tape with metal pole by welding. The joint should be protected with an application of oily paint.

-Procurement and installation measuring joint complete with box for mounting in the wall.

The payment of works shall be made per piece for the completely executed work

# E.5. DIESEL GENERATOR

### Composition

The Diesel Generator Units (DG Unit) shall consist of the following;

    - Diesel Generator Set

    - Fuel Tank

    - Exhaust System

    - Outdoor Weather Protective and Sound Attenuating Enclosure

    - Automatic Transfer Switch (ATS)

    - External Fuel Tank

The DG Unit shall be supplied as a complete pre-integrated and pre-assembled unit.

The DG Unit shall be internationally reputed make. DG units shall be supplied from original suppliers and locally assembled units are not acceptable.

The DG unit shall be designed to be operated at following worse case conditions;

| Altitude Ambient temperatures – Outdoor: Maximum outdoor Maximum outdoor daily average Maximum outdoor yearly average Minimum outdoor Highest one day variation Relative Humidity: Maximum Minimum Yearly average | Up to 1000 meters above sea-level +55o C +40o C +30o C -15o C +25o C 80 % 12 % 35% |
| --- | --- |

### System Conditions

The DG sets shall be designed to be operated under following system parameters;

| Nominal System Voltage | 400 V / 230 V |
| --- | --- |
| Highest System Voltage | 440 V / 253 V |
| Number of Phases | 3 ph, 4 wire |
| Frequency | 50Hz |
| Neutral Point | Solidly Earthed |

### Standards

The DG Units shall be designed, manufactured and tested in compliance with the latest versions of the following standards;

| - IEC 60034 | Rotating Electrical Machines |
| --- | --- |
| - IEC 60085 | Thermal Evaluation and Classification of Electrical Insulation |
| - IEC 60529 | Degrees of Protection provided by Enclosures (IP Code) |
| - ISO 10816 | Specification for Mechanical Performance: Vibration |
| - ISO 3046 | Specification for Reciprocating Internal Combustion Engines |
| - SI 426 | European Commission (dangerous substances) |
|  | (Classification, packing, labelling, and Notification of Regulations 1992. |
| - CIMAC | Congress International des Machines a Combustion Recommendations for Diesel Engine Acceptance Tests Quality assurance |

### Ratings:

The DG Units shall be rated for: 416 V AC, 3 phase, 50 Hz.

Required rated Prime Power Capacities (kVA) at an outdoor operating temperature of 55 deg is as follows.

Bidder should propose generator capacity (KVA) to obtain required prime KVA ratings of 500 KVA, at the maximum outdoor operating temperature. Bidder should also provide calculations and reference graphs, etc, to confirm that the proposed generator is capable of providing the required prime KVA rating.

### Performance

The DG sets shall be capable of delivering rated kVA indicated under item above mentioned point at Prime Power under the service conditions specified in section “Service conditions”.

Voltage regulation: ±0.5 %

Frequency regulation: Random frequency variation with any steady load from no load to full load shall not exceed ±0.25%.

### Diesel Engine

The diesel engine shall comply with the specified International IEC Standards or an equivalent international standard and shall be of the four-stroke, multi-cylinder, water-cooled, cold start, direct fuel injection, compression ignition, and preferably turbo-charged type.

### Speed Governor:

The diesel engine shall be fitted with a speed governor capable of accuracy to Class A2 of ISO 3046/IV. The governor is to be fitted with speed control facilities to enable the engine speed to be adjusted from the local control panel.

### Shutdown System:

The engine shall be fitted with a mechanically operated device which will shut off the fuel supply to engine when any of the specified alarm conditions occur.

### Cooling System:

The cooling system shall be filled with chemically treated water mixture by the equipment supplier. Rotating parts shall be guarded against accidental contact in accordance with standard requirements.

A vertical fan cooled sectional radiator, rated for the tropical site conditions shall be mounted at the end of the combined under base and driven from the diesel engine. The radiator shall be arranged to cool the engine jacket water and lubricating oil. The radiator must be generously sized to permit operation at full load and overload in the specified ambient conditions. The radiator shall be integral with the generating set. The radiator shall be provided complete with fan claw and guards.

### Pumps:

Cooling water, lubricating and fuel oil pressurizing pumps shall be provided and mounted on the engine and shall be gear driven from the crankshaft.

### Lubrication:

Lubrication shall be by means of an engine-driven gear pump and the system shall include full flow oil filters with replaceable elements.

### Safety Guards:

All moving parts shall be adequately guarded, in order to prevent danger to personnel.

### Fuel:

The engine shall be designed for operation on diesel fuel.

### Lubricating and Fuel Oil Filters:

The lubricating and fuel oil filters shall be of the fuel flow type.

### Air Filters:

Air filters shall be suitable for use in the environmental conditions which are likely to arise locally and the service conditions described.

### Starting System:

The set shall be supplied with a completely self-contained starting system consisting of an engine driven dynamo, a lead acid battery and battery charger.

The starting system shall be designed such that at engine speeds in excess of the minimum firing speed it shall be impossible to complete the starting circuit. The starting system shall preclude excessive consecutive starting attempts.

### Exhaust System:

The engine shall be efficiently silenced and be complete with primary and terminal silencer arrangements.

### Alternator

The alternator shall be synchronous, with brushless excitation type and shall comply with the relevant requirements of Specification IEC 60034 or an equivalent international standard.

The alternator shall be designed for operation of 10% engine overload at any power factor between unity and rated power factor for a maximum period of one hour in any 12-hour period as permitted by ISO 3046/II.

The alternator shall be rated for IP-23 protection. The insulation of the winding shall be class H. All winding shall be tropicalized and suitably impregnated to withstand the site ambient conditions.

The alternator shall be complete with all necessary cooling fans, excitation and voltage regulating equipment. The alternator shall be capable of maintaining its continuous maximum rated output when operating within + 5% of rated voltage and at rated power factor.

The alternator shall be brushless rotating field, self-exciting and self-regulating type complete with permanent magnets and fully connected damper windings. The stator winding shall be star- connected and shall be brought out together with the neutral point to terminals located in a sheet steel box mounted on top of the generator to facilitate connection of a power cable of suitable capacity.

The following protection shall be provided for the alternator:

    - Over Current Protection

    - Earth Fault Protection.

### Automatic Transfer Switch (ATS)

The ATS shall comply with IEC 60947 or equivalent international standard. The separately mounted generator control cubicle and ATS panel shall be of sheet steel vermin proof with lockable hinged front doors.

A Four pole circuit breaker and auto transfer switch should be provided rated for full load of the current (+ 10% overload).

The ATS equipment shall be of 3 attempt type and capable of sensing single phase and three phase failure of main supply or any variation in main supply voltage. The main supply and generator supply contactors or Solenoid/Motor operated change over switch shall be of fool proof design with mechanical and electrical interlock.

### Mounting

Complete unit to be mounted on robust skid frame. Vibration mountings to be used where required.

Skid frame to be dimensioned to accommodate generator/alternator assembly, all accessories, sound proof canopy. Skid frame to be of rigid construction suitable for locating on level ground surfaces ranging from compacted earth, crushed rock or a concrete pad.

### Fuel Tanks

Built-in Fuel Tank 180 L with whom you should  minimum capacity of not less than 8-10 hours full running time built in fuel tank shall be provided. Design shall be capable of preventing accidental spilling of fuel and hand pump feeding on emergencies is possible.

### Concrete foundation /pad drawings

Detailed drawings of the concrete/pad foundations required for mounting/installation of all equipment shall be provided with all necessary details within three (03) weeks of award of contract.

Outdoor Weather Protective Sound Attenuating Enclosure

The generator set shall be provided with a sound attenuated housing which allows the generator set to operate at full rated load in the ambient conditions. The enclosure shall reduce the sound level of the generator set while operating at full rated load to below 95 dBA at 1 meter from the generator set. Housing configuration and materials used may be of any suitable design which meets application needs, except that acoustic materials used shall be oil and water resistant. No foam materials shall be used.

The enclosure shall include hinged doors for access to both sides of the engine and alternator, and the control equipment. A panel viewing window shall be provided. Key locking door latches shall be provided for all doors. Door hinges shall be stainless steel.

The enclosure shall be provided with an exhaust silencer, which is mounted outside of the enclosure, and allows the generator set package to meet specified sound level requirements. Silencer and exhaust shall include a rain cap and rain shield.

Fire detection

Diesel generators housing shall have fire detection system suitable for use in an area containing diesel fuel. The fire detection system shall cut off the fuel supply from the tank in the event of a fire. The fire detection system shall operate an alarm system. The system shall meet the requirements of Iraqi fire regulations.

Programmed of work

The supplier shall submit a detailed programmed covering the design, manufacture and testing of the diesel generators within two (2) weeks of receipt of the contract award. The reports shall subsequently be submitted on monthly basis, outlining progress and, if necessary explaining deviations from the programmed.

Type tests

Type test reports/certificates of generators need to be submitted with the bid.

Type tests shall be carried out at an independent laboratory or witnessed by a representative of such laboratory.

E. 6 MEASUREMENT, TESTING AND CERTIFICATES

After performing the electrical installation work, the following electrical values should be measured by an independent authorized company:

1 Grounding resistance- lightning and earthing

2. Resistance to insulation on the energy supply cables to the distribution board and the cable

from the distribution board to the ill consumers

3.Measurement of grounding resistance on mechanical and hydraulic equipment, distribution

boards, electrical connectors, potential equalization box, elevator

4. Testing of differential protection switch  FI

5. Measurement of average illuminance of a working surface

6. Preparation of documentation from the first technical inspection of electrical equipment

7. As- built drawings

  - TERMOTECHNICAL INSTALLATIONS

T1	VRF – SYSTEMS ELEMENTS

T1.1 Outdoor Units

All outdoor units are to be permanently marked with an identification number. The removable access panels are also to be marked with the same number. The outdoor units are to be heat pump.

The units shall be air-cooled type incorporating heat exchanger coils manufactured from copper tubes and aluminum fins, factory treated to reduce the effect of atmospheric corrosion. The unit casing shall be manufactured from (70µ) polyester powder coated baked enamel finish sheet steel in order to have a high corrosion resistance and to protect against salt laden environment close to where the units may be installed. The color shall be manufacturer’s standard ‘off white’. The air outlet grilles shall have plastic coated guards.

The outdoor units shall have at least 1 inverter driven compressor electronically controlled and capable of changing speed linearly to follow the variation in cooling and heating requirements.

The capacity control of the outdoor units will be inverter controlled and shall be determined electronically by sensing operational temperatures, pressures and ambient temperature and monitoring requirements for the indoor units.

The units shall be complete with electronic expansion valve(s), oil separator(s), high pressure switches, fan motor safety devices, over current relay, inverter overload protection, fuses, necessary solenoid valves, refrigerant shutoff valves, re-cycling guard timer and all necessary sensors for a safe and trouble-free operation.

The access to the internal components for maintenance purposes shall be by removable panels.

It shall be possible to connect up to 40 indoor units, capacity permitting, to one outdoor unit.

The 5 hp units shall have a single inverter driven scroll compressor and an inverter driven variable speed propeller type fan.

The 8, & 10 12 and 14hp units shall have two scroll compressors and will be capable of operating on one compressor under emergency condition in case the inverter compressor fails.

One compressor shall be inverter driven capable of ‘Soft start’. The other compressor/s shall be on/ off type. These units will incorporate one inverter driven variable speed propeller type fan.

The fan will be capable of overcoming a minimum of 58 Pascal of external static pressure.

The outdoor unit shall have full capacity control to meet the load fluctuation and indoor unit individual control.

T1.2 Four Way Discharge Square Cassette Ceiling Type

The unit casing shall be manufactured from galvanised steel plate and shall be fully insulated. Facility shall be provided for duct connection for introduction of the fresh air in the unit and branch ductwork from the unit.

The fan shall be of the propeller type, statically and dynamically balanced to ensure low noise and vibration free operation.

The heat exchanger coils will be manufactured from copper tubes and aluminium fins.

It shall have electronic expansion valve to control refrigerant flow rate in response to the load variation in the conditioned space. The expansion valve shall be controlled by an integral computerised control system to maintain correct room temperature.

The low-profile dedicated decoration panel shall be provided for each unit. The decoration panel shall incorporate the return air grille and supply air louvers. A facility shall be provided to automatically swing the supply air louvers or lock them at a desired angle to ensure even distribution of the airflow.

A condensate lift pump shall be provided within the unit and shall be capable of discharging at a height of at least 500 mm above the drain outlet.

The condensate shall be drained from the unit using thermally insulated copper tube and run directly to the foul water drain as indicated.

The air filters shall be incorporated within the unit and shall be mould resistant washable resin net type.

T1.3 Refrigeration Pipe Work

The pipe work shall be of refrigerant quality copper to BS2871 Part 2, ASTM 280, and DIN1754/8905 half hard tempered. Soft tempered pipe work may be used where the pipe diameter is 1/4” or 3/8”. Long radius bends shall be formed using pipe bender. The use of short radius pre-formed bends and elbows should be avoided to minimise pressure drop and possibility of leaks.

Oxygen free nitrogen must be passed through the pipe work during all brazing of joints to prevent the formation of oxidisation scale on the inside surface of the pipes.

All pipe work shall be clean, de-hydrated and sealed. Pipe work shall be stored under dry conditions. Any pipe work found to be stored without the end caps should be rejected. Where sections are cut from a new coil any remaining lengths must be re-sealed. During the installation if the system has to be left unattended for any purpose whatsoever, the openings in the systems must be securely sealed.

Pipe work fittings for branching off to indoor units must be original type Branch joints as supplied by the vendor of the VRF system. No other fittings are acceptable. The positioning of these joints shall be strictly in accordance to the manufacturer’s specification. More detailed information can be found in installation manuals available from the vendor of the VRF system.

All pipe work shall be insulated with Armaflex or similar Class-0 type insulation, 13 mm thick. Joints and headers shall be insulated with the pre-formed insulation supplied with these fittings. Insulation exposed to atmospheric conditions shall be protected with two coats of insulation paint. All insulation joints shall be made using adhesive and care should be taken that every part of insulation is sealed to maintain a vapour barrier.

The pipe work must be supported through its entire length according to good refrigeration practice. However, the brackets must not be positioned directly on the joints or headers. On horizontal pipe work the bracketing should be over the insulation to allow pipe movement due to contraction and expansions. The vertical pipe work shall be bracketed at no more than 1000 mm centres. The horizontal pipe work shall be bracketed at no more than 1500 mm centres.

The pipe work layout and the pipe sizing shall be according to the diagrams supplied by the vendor of the VRF system.

All installed pipe work lengths are to be accurately measured and recorded on the commissioning form. This information is required for accurate calculation of the additional refrigerant charge for the system. The weight of the additional refrigerant must also be recorded for future reference.

T1.4 Pressure Testing, Evacuation and Commissioning

After Installation of pipe work, and prior to sealing of insulation joints, pipe work should be pressure tested to 38 bars, held for 24 hours and checked for leaks, vacuumed/dehydrated to –752 mm Hg and held at that setting for 1 to 4 hours depending on the pipe length. The detailed information can be found in the installation and commissioning procedures available from the vendor of the VRF system.

T1.5 Wiring

A fused 415 V - 3 Phase, N + E power supply with external isolator shall be made available for each outdoor unit. The fuse rating for the 5 hp outdoor unit shall be 20 Amps, the 8 and 10 hp outdoor units shall be 32 amps and the 12 and 14 hp units shall be 40 Amp. All fuses / circuit breakers should be motor rated.

A fused 240 V - 1 Phase, N + E Power supply shall be made available for each indoor unit, the HR box and the centralised control system. It is a normal practice to run 15 amps ring main for the indoor units and HR boxes and a 5 Amp fused spur provided local to each item.

Control cable to the following specification shall be used: 2 core PVC shielded cable sized between 0.75 mm2 and 1.25 mm2.

Control and power cables must not be installed alongside each other as interference in the signal wiring caused by electrostatic and electromagnetic coupling can occur.

The table below indicates manufacturer’s recommendation as to the appropriate spacing of control and power cables where these run side by side:

| Current capacity of the power cables |  | Spacing |
| --- | --- | --- |
|  | 10 amp or less | 300 mm |
| 100 v or more | 10 - 50 amps | 500 mm |
|  | 50 -100 amps | 1000 mm |
|  | 100 amp + | 1500 mm |

The control cables shall be installed on metal cable trays or conduits. Care must be taken to ensure that they are not tied together or packed tightly.

T1.6 POLYPROPYLENE (PP) PIPES FOR CONDENSATE REMOVAL NETWORK

Procurement and installation of the polypropylene (PP-R) pipes, including fittings, for cold (condensate water) piping system, must be all in accordance with ISO 15874. Works include all activities required for installation cold water piping system and shall be implemented fully in accordance with manufacturer’s instruction. Piping system shall sustain working pressure of 10 bars (NP10)

T2.0 Electric Heaters – Convectors Type

The following installations for electric heating shall be installed:

Electric panel heater will wall mounted type. The panels are used to cover the heating losses in offices and as stand-by option.

Electric heater-convector consist

-	front panel,

-	sheathed heating element,

-	air outlet grid,

-	on/off mode switch

-	temperature regulation knob

-	over temperature cut-out device

# 4.4. FIRE FIGHTING

THE FOLLOWING REGULATIONS, RULES, NORMS AND LAWS WERE USED IN THE PREPARATION OF THE REPORT:

1. Law on firefighting Official Gazette No. 67/2004, 81/2007, 55/13, 158/14, 193/15 and 39/16 purified text 168/2017 and amendments and additions in 2019

2. Law on Protection and Rescue Official Gazette no. 36/2004 and 49/2004, revised text 93/2012 and Amendment in Official Gazette no. 41/14,129/15,71/16,106/16 and 83/18

3. Instructions for the content of the report on protection against fires, explosions and dangerous substances Official Gazette no. 139/2010

4. Rulebook on the method of determining the places where fire protection devices and installations, other fire fighting equipment, means of extinguishing fires and fire extinguishers, their maintenance in proper condition, special marking and availability for use must be located. .newspaper no. 74/2006 and amendments 76/2007

5. Rulebook on the technical standards for the hydrant network for extinguishing fires Official Gazette no. 26/2018

6. Rulebook for a closer determination of the choice of the types and quantities of fire extinguishers that legal entities and citizens should have at their disposal, as well as for determining the criteria that must be met by legal entities that perform service inspection and control testing of fire extinguishers, relating to technical equipment and work space (Official Gazette No. 26/2018)

7. Rulebook on essential requirements for fire protection of construction facilities, Official Gazette no. 94/2009

8. Rulebook on measures for protection against fires, explosions and dangerous substances, Official Gazette no. 231/2020

9. Decree on the method of applying the measures for protection and rescue during planning and arrangement of the space and settlements, in the projects and during the construction of the facilities, as well as participation in the technical review.

10. Other literature and positive regulation

Appendix 1 Table Division of objects according to purpose

Annex 2 Category of technological process

MKS.U.J1.240

The legal entity must act in accordance with the same and other regulations:

Rulebook on the form of the forms, the way of keeping records of fires, explosions, interventions for extinguishing fires and other events Official Gazette no. 60/2006.

This specification shall be followed in comply with the Drawings, the Bill of Quantities and other Contract Documents as well as standards МКS EN 12 381 - calculation of heat losses, (МКS EN 69 46, 7345, 9246, 9229, 1011 - 1/2, 13789, 14683). Any equipment mentioned in this specification that is not provided in Main Design (BoQ and Drawings) shall be considered as informative and as guidance for future reconstruction, renovation or changes during the performance on proposal of the Contracting Authority/Supervisor in accordance with the Designer.

Sirens:

It should be possible to select siren tones and volume from the control panel. Up to two different tones will be selectable for each siren and configured to work with different cause and effect scenarios.

Alarm indicators:

It should be possible to configure an individual LED extension to be triggered by any of several detectors.

Isolation – fire alarm control panels shall permit isolation of any individual device, zone, section or area. Any insulation must be capable of being regenerated after a predetermined period of time.

Renovation Mode - fire alarm control panels include a renovation mode that can be set during a temporary renovation. This mode sets all detectors in the selected area to a lower sensitivity "Renovation" set parameter.

Test modes - fire alarm control panels will allow the following tests to be performed:

1) test lamps - The control panel should include a control button, which will illuminate all panel indicators and highlight the completeness of the screen.

2) detector test - The control panel can be set in detector test mode. This increases the sensitivity of all detectors in that zone by setting the robustness parameter. During the test, the detector alarm indicator will be illuminated, but the sirens and controls will not activate. More basic sirens connected directly to the detector will operate briefly.

3) installation test - Control panel to be able to set zones in detector test mode. This increases the sensitivity of all detectors in that zone by setting the robustness parameter. On the indicator alarm test the detector will be illuminated and all programmed sirens and controls should operate as required.

4) Walk test - the operation panel can set groups in test mode. When the detector is activated, the alarm siren is activated for 10 seconds.

5) Circuit card detection (4 circuits)

6) circuit card extension

7) Circuit card detection for interactive addressable detector series (1 cycle)

8) Circuit card detection for interactive addressable detector series (1 template)

9) Circuit card detection for SynoLOOP addressable array detectors (4 circuits)

10) I / O card (programmable)

11) 2 x 4 siren cards.

12) Network cards.

13) RS232 interface card

14) RS485 interface card

ADDRESSABLE FIRE PANEL

Installation of  Addressable fire panel  with 1 loop / 250 addressable PP devices, capacity of the current circuit 500 mA, 8 zones, 4 relay outputs, 2 outputs (controlled, programmable, relays), Power supply (18-26) V /1.5 A, event memory 1240 events, LCD display 4* 20 characters , multilingual, programming – DMT Tech sowtver, R5485 output interface. Made according to EN-45-2 and EN-45-4

ADDRESSABLE OPTICAL – SMOKE DETECTOR

Intelligent devices with integrated algorithms for comparison with real sensor signals, ensuring fast and reliable detection. Detectors should meet and be approved by EN54-7. The detector should be designed to have a high level of tolerance to dust, dirt, temperature fluctuations and air currents. In addition, the detector should contain:

1. Selection of specific application set parameters.

2. Communication of 3 different danger levels for differentiated alarm activations

3. Ability to detect if the detector is in an inappropriate environment and give a special warning about it on the panel

4. Gradual penetration of dust and dirt, to ensure a consistent level of detection over time. When the detector reaches a tolerance point where it can no longer tolerate the possibility of detection by a special warning signal given to the control equipment.

5. Compound Insulator Short Circuit. Separately controlled remote output indicator for activation, or other detectors. Indicator with put response with 360 viewing angle. The operating temperature ranges from -10 C to + 55 C. EMC compatibility 50V / m

ADDRESSABLE HEAT DETECTOR

Heat detectors should be intelligent devices with integrated algorithms for comparison with real sensor signals ensuring relevant detection. Detectors should meet and be approved by EN54-5. In addition, the detector should contain:

1. Application selection for a specific parameter set

2. Communication of 3 different danger levels for differentiated alarm activations.

3. Internal fault monitoring with special signal fault report to the control panel.

4. Integrated short circuit isolator.

5. Separate controlled remote output indicator for activation by this or other detectors.

6. integral indicator with 360 ° viewing angle.

7. Operating temperature range from -10 ° C to + 55 ° C

8. EMC compatibility at 50V / m

ADDRESSABLE MANUAL CALL POINT (AMCP)

Installation of a manual call point with shrinkable glass type suitable for flat or surface mounting and approved by EN54-11 and EN54-17. The manual call point should also contain a test button for quick testing of the device, without removing the glass. The manual dialer also consists of the following:

1. Integrated short circuit isolator.

2. Alarm indicator.

3. Space for adding an additional protective door.

Operating temperature: -25 ° C to + 70 ° C. EMC compatibility at least 50V / m. Full protection of at least IP44 protection

ADDRESSABLE SOUNDER - INTERNAL

Installation of an addressable alarm siren, which should be for power supply in a loop. They should meet the requirements to be approved by EN54-3. In addition they should:

- Have a built-in short-circuit isolator in the event of a short-circuit on the loop, the siren / signal must continue to sound.

- Have locking capability to prevent unauthorized removal.

- To have 11 programmable tones to choose from the panel.

- To have the ability to choose between warning and evacuation tones.

- Be fully synchronized with other sirens connected to the control panel.

- To have 3 settings for selecting the volume from the panel.

- To be able to provide a power of at least 99dBA at 1m.

- To be painted red with RAL 3000

- Operating temperature in the range from -25 ° C to + 70 ° C

- To have a minimum of EMC compatible at 50V/m

ADDRESSABLE SOUNDER WITH STROBE - OUTDOOR

Supply and installation of flasher alarm sirens shall be addressable units connected and powered directly on a loop. They should meet the requirements and be approved by EN54-3 and EN54-17.

In addition they should:

Supply and installation of flasher alarm sirens shall be addressable units connected and powered directly on a loop. They should meet the requirements and be approved by EN54-3 and EN54-17. In addition they should:

- Operating temperature in the range from -25 ° C to + 65 ° C

- To be painted in orange transparent color

- Have a built-in short-circuit isolator in the event of a short-circuit on the loop, the siren / signal must continue to sound.

- Have locking capability to prevent unauthorized removal.

- To have 11 programmable tones to choose from the panel.

- To have the ability to choose between warning and evacuation tones.

- Be fully synchronized with other sirens connected to the control panel.

- To have 3 settings for selecting the volume from the panel.

- To be able to provide a power of at least 99 dBA at 1m.

- To have a maximum output of at least 3.2cd

- To be painted in orange transparent color

- To have a working temperature range

- Minimum EMC compatibility of 50V/m

ADDRESSABLE INPUT MODULE

Installation of input modules that must comply with the requirements and be approved by EN54-17. Input modules should be connected directly to the loop and require no further power connections. Each input module should take one address, but has four separate programmable inputs. Input modules will additionally include:

1. Inputs for short and open circuit.

2. Inputs can be configured for normally open and normally closed operation.

3. Integrated short circuit isolator.

4. LED indication of normal, fault, test, and activation conditions.

5. Possibility of configuration for safe operation in case of failure.

6. Programmable filter activation delay from  0-240 seconds.

7. The modules must be mounted in an IP54 housing with a clear cover to indicate the status of the device.

8. Where modules are to be placed outside or in other areas, where they are likely to be wet or sprayed with water spray they should be mounted in an IP66 enclosure with a clear cover to indicate the status of the device.

9. The modules should additionally be suitable for DIN rail mounting.

10. Operating temperature: -25 ° C to + 60 ° C

11. EMC compatibility: 50V / m

ADDRESSABLE INPUT / OUTPUT MODULE

Input / output modules should comply with the requirements and be approved by EN54-17. Input / output modules should be connected directly to the loop and require no further power connections. Each input/output module should take one address, but has four separate programmable inputs and four separate programmable outputs. Input / output modules additionally include:

1. Short and open circuit inputs.

2. Inputs can be configured for normally open and normally closed operation.

3. Outputs Payment to be rated at 250VAC 4A resistive and 30Vdc 4A clean contacts.

4. The outputs have a choice of continuous or pulse operation. Pulse duration to be a choice between 1 and 20 seconds.

5. Composite short circuit insulator.

6. LED indication of normal, fault, test, and activation conditions.

7. Possibility of configuration for safe operation in case of failure.

8. Programmable filter activation delay from 0-240 seconds.

9. The modules should be mounted in IP54 housings with a clear cover to indicate the status of the device.

10. Where modules are to be placed outside or in other areas, where they are likely to be exposed to moisture or splashed with water they should be mounted in an IP66 enclosure with a clear cover to indicate the status of the device.

11. Modules should additionally be suitable for DIN rail mounting.

12. Operating temperature: -25 ° C to + 60 ° C

13. EMC compatibility: 50V / m

FIRE EXTINGUISHING SYSTEM CABLE

1. The installation must be in accordance with the latest edition of IEE regulations and in accordance with the requirements of the country.

2. Surface cabling shall be neatly routed and securely fixed at appropriate intervals in accordance with the manufacturer's recommendations.

3. Connections in cables other than those within the equipment should be avoided whenever possible.

4. Where a cable passes through an external wall it should be contained by a smooth sheath of metal or other non-hygroscopic material sealed into the wall. This material will have an outward slope and should be sealed with a suitable waterproofing component.

5. Where cables, conductors or wiring pass through floors, walls, partitions or ceilings the surrounding hole should be made of good fireproof material with sufficient fire resistance to maintain the integrity of the building.

6. Each junction box shall have the legend "Fire System" on the front page.

7. All wiring shall be secured by identifying a permanent mark within 25mm of the break.

8. A special color will be used during the installation of the fire conductors.

9. Conducting electrical energy in the enclosures will be organized to allow access to the equipment for adjustment and maintenance.

FIRE SYSTEM MONITORING SOFTWARE, TECHNICAL DOCUMENTATION, DETECTION SYSTEM INTEGRATION, COMMISSIONING

Installation of appropriate to the selected equipment, software. The system should be suitable to be controlled by a remote computer using software that can be dialed with the connected panel to enable remote inquiry and operation. The software should be set up to appear as a direct copy of the control panel and be capable of displaying all information and controlling all features of the panel itself.

The entire system will be inspected and tested to ensure that it operates in accordance with this specification and country requirements. Especially that:

1. All manual call points and automatic fire detectors are functioning properly.

2. All devices carry an accurate identification label.

3. All manual call points and automatic fire detectors, when operating, result in correct text and zone marking on all indicating equipment.

4. The sound pressure level meets the requirements of the country.

5. The connection to the ARC (Fire Service) is working properly.

6. System causes and effects meet the requirements of this specification.

7. All manual call points and automatic fire detectors meet the requirements of the country.

8. All auxiliary functions such as lift-returns, boiler shut-off and mechanisms for etc.9. All fault indicators and their relevant circuits are verified by simulating appropriate fault conditions.

10. Read and record all insulation resistance, ground continuity and circuit impedance.

The internal hydrant network consists of a pipe distribution of galvanized pipes and hydrants located in a hydrant cabinet.

The hydrant cabinet with dimensions 500/500/150 mm inside has a ball valve, a coiled hose with a length of 15 m and the same is marked with the letter H.

Hydrants are placed in stairwells, corridors and evacuation routes. The distance between hydrants is determined so that the entire surface to be protected from fire should be covered with a jet of water (the length of the hose is 15 m, and the length of a compact jet 5 m)

The smallest diameter of an internal hydrant pipe should be DN50. In accordance with the "Rules for Technical Norms for Fire Extinguishing Hydrant Networks" for buildings up to 22 meters, simultaneous operation of 2 hydrants of 2.5 l/s of water each, i.e. a total of 5 l/s, is required at the minimum pressure of the highest (farthest) 2.5 bara hydrant.

The external hydrant network consists of overhead hydrants or underground hydrants if they count on turnover.

The distance between two hydrants must not exceed 80 m.

Hydrant distance from the wall of the building must be at least 5 meters, and the maximum allowed distance of 80 m

The smallest diameter of the external hydrant pipe is DN100.

AS-BUILT DRAWINGS

Drawings/design documents related to final executed works according to the design and its changes during the execution of the works as per PRAG and National legislation.